## Basis & Assumptions (2) (hidden)
Assumptions and Inputs considered for MV & LV cable sizing
1) | All MV & LV cables are considered to be laid in Air / Trench with cover Cable Tray and de-rated accordingly.
2) | All MV & LV multi-core cables are considered to be laid on touching formation and de-rated accordingly.
3) | All MV single core cables are considered to be laid in Trefoil Formation with 150mm spacing and de-rated accordingly.
4) | All LV single core cables are considered to be laid in Trefoil Formation and de-rated accordingly.
5) | Over all de-rating factor considered as mentioned below based on laying condition & method of installation: LV Multi core cable - 0.66 LV Single core cable - 0.9 MV Multi core cable - 0.664 MV Single core cable - 0.819
6) | The % voltage drop is limited to 3% for outgoing motor feeders , 2.5% for outgoing Power feeders and 2% to incoming feeders.
7) | The % voltage drop is limited to 15% for motor feeders during starting.
8) | For both MV & LV Cable sizing all required datas are taken from reference Catalogue (KEC/RPG Make Catalogue). Further final Cable sizing/BOQ shall be updated based on final vendor data during Detail Engg. Stage.
9) | Desalination package both MV & LV power cable has kept under hold & same shall be revised after the finaliziation of scope.
10) | Wherever the location of load is unknown, an approximate location is assumed and % voltage drop is calculated.
11) | This cable sizing is done based on the "Electrical Load List, Rev-1". And same will be revised after finalization of final Loas list.
12) | The below mentioned pachages are part of Vendor scope, henece respective package Cable sizing / cable boq has not included. 1. Ammonia Storage area, 2. ASU Package, 3. Nitrogen Package, 4. Flare area Package, 5. Cooling tower Package. 6. ETP Package. 7. Desalination Sea Water Treatment Package. 8. Sea Water Intake system. 9. Electrolyzer Area Package.
from ups sub db to I&C instrument cable lnot considered

## Basis & Assumptions
Basis & Assumptions considered for MV & LV cable sizing
1) | All MV & LV cables are considered to be laid in Air / Trench with cover Cable Tray and de-rated accordingly.
2) | All MV & LV multi-core cables are considered to be laid on touching formation and de-rated accordingly.
3) | All MV single core cables are considered to be laid in Trefoil Formation with 150mm spacing and de-rated accordingly.
4) | All LV single core cables are considered to be laid in Trefoil Formation and de-rated accordingly.
5) | Over all de-rating factor considered as mentioned below based on laying condition & method of installation: LV Multi core cable - 0.587 LV Single core cable - 0.721 MV Multi core cable - 0.599 MV Single core cable - 0.738
6) | The % voltage drop is limited to 3% for outgoing motor feeders , 2.5% for outgoing Power feeders and 2% to incoming feeders.
7) | The % voltage drop is limited to 15% for motor feeders during starting.
8) | For both MV & LV Cable sizing all required datas are taken from reference Catalogue (KEC/RPG Make Catalogue). Further final Cable sizing/BOQ shall be updated based on final vendor data during Detail Engg. Stage.
9) | 1). All incoming cable from solar, Grid, BESS to 33kV Switchgear (MSB) cable is part of Vendor/ACME scope henace same sizing/BOQ not considered. 2). In Desalination package: a) Incoming Cable from LV VFD to PMCC-4, 11kV Switchgaer to MV VFD's, both MV & LV power cables are inculded in the sizing/BOQ. b) Further from PMCC to Motor/LCS, from LV VFD to motor/LCS, from MV VFD to motor/LCS both MV & LV power cable BOQ is part of Vendor/ACME scope hence same has not included in the sizing/BOQ.
10) | Wherever the location of load is unknown, an approximate location is assumed and % voltage drop is calculated.
11) | This cable sizing is done based on the "Electrical Load List, Rev-1". And same will be revised after finalization of final Loas list.
12) | Cable from UPS DB/ Sub UPS DB to Instrument is not included in this sizing & same shall be considered in Instrument cable schedule/BOQ.
13) | The below mentioned packages are part of Vendor scope, henece respective package Cable sizing / cable boq has not included. 1. Ammonia Storage area, 2. ASU Package, 3. Nitrogen Package, 4. Flare area Package, 5. Cooling tower Package. 6. ETP Package. 7. Desalination Sea Water Treatment Package. 8. Sea Water Intake system. 9. Electrolyzer Area Package.

## Tray Sizing (hidden)
Cable Tray Sections |  | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | G1 | G2 | G3 | G4 | H | I | J | J1 | J2 | J3 | K | L | L1 | L2 | L3 | L4 | M | N | O | O1 | P | Q | Q1 | Q2 | Q3 | R | R1 | R2 | S | T
33kV MV Power Cable Trays
MV Cable sizing-33kV | Total Cable Dia | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total Cable Tray Dia required with 20% Margin | with 20% marging | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
33kV MV Power Cable Trays |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11kV MV Power Cable Trays
MV Cable sizing-11kV |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total Cable Tray Dia required with 20% Margin |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11kV Power Cables - Ladder Type Tray | 600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | #REF! | #REF! | #REF! | #REF! | #REF! | 2 | 0 | 0 | 0 | 2 | 0 | 1 | #REF! | 0 | 0 | 0 | 0 | 1 | 1 | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | 0 | #REF! | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | 0 | #REF! | 0 | 0 | 0 | #REF! | #REF!
| 450 | [13 empty] | #REF! | [9 empty] | #REF! |  | #REF! | [14 empty] | #REF!
| 300 | [5 empty] | 1 | #REF! | #REF! | #REF! | 1 | #REF! | 1 |  |  | #REF! | #REF! | #REF! | [10 empty] | #REF! | #REF! | #REF! | [12 empty] | #REF! |  | #REF! | #REF! | #REF!
LV Power Cable Trays
LV Cable sizing_SS-1_Power Cables |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
LV Cable sizing_SS-2_Power Cables |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
LV Cable sizing_SS-3_Power Cables |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
LV Cable sizing_SS-4_Power Cables |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
LV Cable sizing_SS-5_Power Cables
LV Cable sizing_SS-6_Power Cables
Total Cable Tray Dia required for LV power Cable |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total Cable Tray Dia required with 20% Margin |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
LV Power Cables - Ladder Type Tray | 600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | #REF! | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | 7 | 4 | 3 | 2 | 1 | 0 | #REF! | #REF! | 1 | 0 | 1 | 0 | 1 | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 5 | 5 | 4 | #REF! | 2 | #REF!
| 450 | [12 empty] | 1 |  |  |  | #REF! | [23 empty] | #REF!
| 300 | [7 empty] | #REF! | [5 empty] | 1 | 1 | 1 |  |  |  | 1 | #REF! | 1 | #REF! | 1 |  |  |  |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  |  | #REF! | 1 |  |  | 1 |  | 1
LV Control Cables - Ladder Type Tray | 600 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0
| 450 | [16 empty] | 1
| 300 | [17 empty] | #REF! |  |  | #REF! |  | #REF! |  | 0 | 0 |  |  | #REF! | [7 empty] | 0 | #REF! | #REF! |  | 1 | #REF! | 1 | 1 | 1 | 1 | 0 | 1 | 1
Instrumentation Cable Trays |  | 1 | 3 | 3 | 14 | 8 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [19 empty] | 2 | 2 |  | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1
|  | 1 | 2 | 12 | 2 | 8 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [19 empty] | 2 | 2 |  | 2
Instrumentation Cable Trays
IS Cable Tray | Total Cable Dia
600
450
300
Non IS Cable Tray | Total Cable Dia
600
450
300
F&G Cable Tray | Total Cable Dia
600
450
300
FOC & Telecom Cable Tray | Total Cable Dia
600
450
300
133.5
136.5
172.5
189.5
214.5
204.5
SS-2 to Admin
SS-2 to Canteen
SS-2 to Fire room
SS-2 to Store
SS-2 to OHC
SS-2 to Whorehouse

## Catalogue Aluminium
LV Cable Catalogue (KEC/RPG Make Catalogue Attached) | [7 empty] | DERATING FACTORS
1-core cable |  |  |  |  | 0.6/1.0 kV
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | LV | XLPE | Ambient temperature (50°C) (K1) | Grouping factor (K2) 4 trafoil groups, 6 tier trays with Touching |  | Ground temperature (35°C) (K3) | Depth of laying (900 mm) (K4) |  | Thermal resistivity of ground (1.2 K.m/W) (K5)
| Air | Ground | Duct | [6 empty] | Single core (Trefoil Formation with Touching) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 185 | 370 | 290 | 224 | 0.21 | 0.0875 | 26 | 690/400V | AIR | 0.89 | 0.81 | 0.66 | NA | NA | NA
1C X 240 | 445 | 340 | 283 | 0.16 | 0.0866 | 28 |  | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98 | 1.5 | 1.09 | 1.05
1C X 300 | 514 | 382 | 317 | 0.128 | 0.0857 | 31 |  | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98 | 2.5 | 1.09 | 1.05
1C X 400 | 605 | 437 | 370 | 0.1 | 0.0855 | 34 |  | Trench with cover | 0.89 | 0.81 | 0.66 | NA | NA | NA | 4 | 1.09 | 1.05 | 0.76
1C X 500 | 704 | 500 | 428 | 0.0774 | 0.0851 | 38 | [8 empty] | 6 | 1.09 | 1.05
1C X 630 | 822 | 565 | 464 | 0.06 | 0.0843 | 42 | [8 empty] | 10 | 1.09 | 1.06
[15 empty] | 16 | 1.09 | 1.06
2-core cable |  |  |  |  | 0.6/1.0 kV | [9 empty] | 25 | 1.09 | 1.08
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | [8 empty] | 35 | 1.09 | 1.08
| Air | Ground | Duct | [11 empty] | 50 | 1.09 | 1.08
2C X 1.5 | 29 | 33 | 29 | 15.5 | 0.108 | 12 | [8 empty] | 70 | 1.1 | 1.08
2C X 2.5 | 39 | 43 | 37 | 9.48 | 0.1007 | 13 | [8 empty] | 95 | 1.1 | 1.08
2C X 4 | 48 | 54 | 46 | 5.9 | 0.0947 | 14 | [8 empty] | 120 | 1.1 | 1.08
2C X 6 | 59 | 66 | 58 | 3.94 | 0.0902 | 15 | [8 empty] | 150 | 1.1 | 1.09
2C X 10 | 62 | 70 | 57 | 3.94 | 0.0852 | 17 | [8 empty] | 185 | 1.1 | 1.09
2C X 16 | 79 | 90 | 75 | 2.44 | 0.0815 | 18 | [8 empty] | 240 | 1.1 | 1.09
2C X 25 | 108 | 117 | 99 | 1.54 | 0.0816 | 20 | [8 empty] | 300 | 1.1 | 1.09
2C X 35 | 143 | 140 | 117 | 1.11 | 0.0794 | 21 | [8 empty] | 400 | 1.11 | 1.1
2C X 50 | 173 | 168 | 143 | 0.82 | 0.0792 | 24 | [8 empty] | 500 | 1.11 | 1.1
2C X 70 | 212 | 202 | 177 | 0.567 | 0.0752 | 27 | [8 empty] | 630 | 1.11 | 1.1
2C X 95 | 257 | 243 | 217 | 0.41 | 0.0734 | 30
2C X 120 | 295 | 273 | 247 | 0.324 | 0.0726 | 32
2C X 150 | 342 | 310 | 305 | 0.264 | 0.0732 | 35
2C X 185 | 395 | 350 | 345 | 0.21 | 0.0727 | 39
2C X 240 | 465 | 401 | 393 | 0.16 | 0.0719 | 44
2C X 300 | 532 | 458 | 453 | 0.128 | 0.0711 | 48
2C X 400 | 622 | 505 | 553 | 0.1 | 0.0705 | 54
3-core cable |  |  |  |  | 0.6/1.0 kV
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
3C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13 | [11 empty] | 13.2
3C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 14 | [11 empty] | 16.8
3C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 15 | [11 empty] | 22.8
3C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 16 | [11 empty] | 30.6
3C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 19 | [11 empty] | 36
3C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 19 | [11 empty] | 42
3C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 21 | [11 empty] | 57
3C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 23 | [11 empty] | 70.2
3C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 26 | [11 empty] | 84.6
3C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 30 | [11 empty] | 106.2
3C X 95 | 221 | 198 | 168 | 0.41 | 0.0734 | 33 | [11 empty] | 132.6
3C X 120 | 257 | 225 | 189 | 0.324 | 0.0726 | 35 | [11 empty] | 154.2
3C X 150 | 293 | 252 | 210 | 0.264 | 0.0732 | 39 | [11 empty] | 175.8
3C X 185 | 338 | 285 | 243 | 0.21 | 0.0727 | 43 | [11 empty] | 202.8
3C X 240 | 401 | 330 | 282 | 0.16 | 0.0719 | 48 | [11 empty] | 240.6
3C X 300 | 459 | 371 | 316 | 0.128 | 0.0711 | 53 | [11 empty] | 275.4
3C X 400 | 536 | 423 | 282 | 0.1 | 0.0705 | 59 | [11 empty] | 321.6
4-core cable |  |  |  |  | 0.6/1.0 kV
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
4C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
4C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
4C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
4C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
4C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 20
4C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 21
3.5C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 25
3.5C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 27
3.5C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 30
3.5C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 36
3.5C X 95 | 221 | 198 | 168 | 0.41 | 0.0734 | 39
3.5C X 120 | 257 | 225 | 189 | 0.324 | 0.0726 | 43
3.5C X 150 | 293 | 252 | 210 | 0.264 | 0.0732 | 48
3.5C X 185 | 338 | 285 | 243 | 0.21 | 0.0727 | 53
3.5C X 240 | 401 | 330 | 282 | 0.16 | 0.0719 | 58
3.5C X 300 | 459 | 371 | 316 | 0.128 | 0.0711 | 64
3.5C X 400 | 536 | 423 | 282 | 0.1 | 0.0705 | 72
5-Core Cable |  |  |  |  | 0.6/1.0 kV
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
5C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
5C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
5C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
5C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
5C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 20
5C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 20
5C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 24
5C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 26
5C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 29
5C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 33

## Sheet2 (hidden)
24 nos | 88 | 24 |  | 2112 | 2534.4 |  | 2 nos
7 nos | 86 | 7 |  | 602 | 722.4 |  | 2 nos
8 nos | 88 | 8 |  | 704 | 844.8 |  | 2 nos
7 nos | 86 | 7 |  | 602 | 722.4 |  | 2 nos
Electrolyzer Area Cable Tray requirement
Main entry
| 33kV | 5.428 | Cable Trench | Ladded | 600mm | 6
| LV | 1 | Cable Trench | Ladded | 600mm | 1
| Control | 1 | Cable Trench | Perforated | 600mm | 1
| I&C | 2 | Cable Trench | Perforated | 600mm | 2
Package-1 & Electrolyzer building
| 33kV | 2.612 | Cable Trench | Ladded | 600mm | 3
| LV | 1 | Cable Trench | Ladded | 600mm | 1
| Control | 1 | Cable Trench | Perforated | 600mm | 1
| I&C | 2 | Cable Trench | Perforated | 600mm | 2
Package-2 & 3
| 33kV | 2.816 | Cable Trench | Ladded | 600mm | 3
| LV | 1 | Cable Trench | Ladded | 600mm | 1
| Control | 1 | Cable Trench | Perforated | 600mm | 1
| I&C | 2 | Cable Trench | Perforated | 600mm | 2
Package- 3
| 33kV | 1.408 | Pipe Rack & Cable Trench | Ladded | 600mm | 2
| LV | 1 | Pipe Rack & Cable Trench | Ladded | 600mm | 1
| Control | 1 | Pipe Rack & Cable Trench | Perforated | 600mm | 1
| I&C | 2 | Pipe Rack & Cable Trench | Perforated | 600mm | 2

## LV Cable sizing_SS-1
LV POWER CABLE SIZING
Sl. No |  |  | LOAD | [12 empty] | SHORT CIRCUIT CURRENT WITHSTAND CAPABILITY |  |  | CABLE DATA | [14 empty] | DERATING FACTOR | [5 empty] | CURRENT CARRYING CAPACITY |  |  | RUNNING CONDITION VOLTAGE DROP |  | MOTOR STARTING VOLTAGE DROP |  | Selected Cable Size
| Tag No. | From | Description | Equipment Location | Bus | Type of feeder | Rated power | UNIT (kW / kVa) | 3Phase / 1Phase | Rated Voltage (V) | Power factor | Efficiency | Rated full load current | Motor starting current | Motor starting power factor | Short circuit current of switchboard (kA) | Short circuit current withstand duration (sec) | Minimum size required for Short circuit withstand capacity (Sq.mm) | Installation | No. of Cores | Size in (Sq.mm) | Cable size | Cable size With (PE) Core | Cable Voltage (kV) | Current Rating of the Cable (A) | Cable resistance at 90°C (Ohm / Ph / km) | Cable reactance at 50Hz (Ohm / Ph / km) | Cable Length with in Electrical Building (m) | Cable Length from Electrical Building to Equipment (m) | Cable length Riser & Dropper (m) | Cable length both side dropping & Termination (m) | Spare 10% | Cable length for each run (m) | Ambient temperature (K1) | Grouping factor (K2) | Ground temperature (K3) | Depth of laying (K4) | Thermal resistivity of ground (K5) | Overall derating factor | Derated current carrying capacity (A) | No. of Runs | Derated current > Rated current | % VOLTAGE DROP DURING RUNNING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT (YES/NO) | % VOLTAGE DROP DURING STARTING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT DURING STARTING CONDITION (YES/NO) | Selected cable size | Selected cable size | Total Cable Length in meters | Remarks
MAIN SUBSTATION
PMCC-1
X | 1401-PM104A | PMCC-1 | BFW PUMP | AMMONIA PLANT | A | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.957 | 133.083 | 798.4979 | 0.2 | 65 | 0 | 0 | AIR | 3C | 185 | 3C X 185 | 3C X 185+PE | 0.6/1.0 | 338 | 0.21 | 0.0727 | 29 | 263 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 185 Sqmm | 1R x 0.6/1kV x 3C x 185+PE Sqmm
X | 1401-PM104B | PMCC-1 | SPARE BFW PUMP | AMMONIA PLANT | B | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.957 | 133.083 | 798.4979 | 0.2 | 65 | 0 | 0 | AIR | 3C | 185 | 3C X 185 | 3C X 185+PE | 0.6/1.0 | 338 | 0.21 | 0.0727 | 38 | 263 | 38 | 8 | 35 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 185 Sqmm | 1R x 0.6/1kV x 3C x 185+PE Sqmm
X | 1401-PM112A | PMCC-1 | CONDENSATE PUMP FOR 1401-C-301 | AMMONIA PLANT | A | MOTOR | 9.3 | kW | 3Ph | 400 | 0.79 | 0.906 | 18.7551 | 112.5307 | 0.2 | 65 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 29 | 309 | 38 | 8 | 39 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50+PE Sqmm
X | 1401-PM112B | PMCC-1 | CONDENSATE PUMP FOR 1401-C-301 | AMMONIA PLANT | B | MOTOR | 9.3 | kW | 3Ph | 400 | 0.79 | 0.906 | 18.7551 | 112.5307 | 0.2 | 65 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 309 | 38 | 8 | 40 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50+PE Sqmm
1 | 1401-PM116A | PMCC-1 | CONDENSATE INJECTION SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 315 | 38 | 8 | 39 | 429 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.72016 | YES | 1.258 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 429
2 | 1401-PM107A | PMCC-1 | PH CONTROL INJECTION SYSTEM PUMP | AMMONIA PLANT | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 266 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.6463 | YES | 1.129 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 385
3 | 1401-PM108A | PMCC-1 | PHOSPHATE INJECTION SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 284 | 38 | 8 | 36 | 395 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.66308 | YES | 1.1583 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 395
4 | 1401-PM106A | PMCC-1 | OXYGEN SCAVENGER SYSTEM PUMP | AMMONIA PLANT | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.65133 | YES | 1.1378 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 388
5 | 1401-PM116B | PMCC-1 | CONDENSATE INJECTION SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 315 | 38 | 8 | 39 | 429 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.72016 | YES | 1.258 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 429
6 | 1401-PM107B | PMCC-1 | PH CONTROL INJECTION SYSTEM PUMP | AMMONIA PLANT | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 266 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.6463 | YES | 1.129 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 385
7 | 1401-PM108B | PMCC-1 | PHOSPHATE INJECTION SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 284 | 38 | 8 | 36 | 395 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.66308 | YES | 1.1583 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 395
8 | 1401-PM106B | PMCC-1 | OXYGEN SCAVENGER SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 268 | 38 | 8 | 35 | 378 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.63454 | YES | 1.1085 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 378
9 | 1401-LFA108 | PMCC-1 | PHOSPHATE INJECTION SYSTEM PUMP | AMMONIA PLANT | B | MOTOR | 0.75 | kW | 3Ph | 400 | 0.73 | 0.825 | 1.7975 | 10.7852 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 284 | 38 | 8 | 37 | 405 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.3781 | YES | 2.4073 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 405
10 | 1401-LFA106 | PMCC-1 | OXYGEN SCAVENGER SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.75 | kW | 3Ph | 400 | 0.73 | 0.825 | 1.7975 | 10.7852 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 268 | 38 | 8 | 35 | 378 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.2862 | YES | 2.2469 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 378
11 |  | PMCC-1 | ELECTRICAL STROKE SETTING DEVICE FOR STEAM CONDENSATE INJECTION UNIT | AMMONIA PLANT | A | MOTOR | 0.01 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.072193 | 0.43316 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 268 | 38 | 8 | 35 | 378 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.089841 | YES | 0.15694 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 378
12 |  | PMCC-1 | STANDBY ELECTRICAL STROKE SETTING DEVICE FOR STEAM CONDENSATE INJECTION UNIT | AMMONIA PLANT | B | MOTOR | 0.01 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.072193 | 0.43316 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.092217 | YES | 0.16109 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 388
13 | 1411-JM001A | PMCC-1 | INSTRUMENT AIR COMPRESSOR -A | INSTRUMENT AIR COMPRESSOR AREA | A | MOTOR | 160 | kW | 3Ph | 400 | 0.86 | 0.964 | 278.5715 | 1671.4288 | 0.2 | 65 | 0 | 0 | AIR | 3C | 300 | 3C X 300 | 3C X 300+PE | 0.6/1.0 | 459 | 0.128 | 0.0711 | 29 | 157 | 22 | 8 | 22 | 238 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.1009 | YES | 8.2047 | YES | 2R x 0.6/1kV x 3C x 300 Sqmm | 2R x 0.6/1kV x 3C x 300+PE Sqmm | 476
14 | 1411-JM001A | PMCC-1 | INSTRUMENT AIR COMPRESSOR -A-SPACE HEATER | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 29 | 157 | 22 | 8 | 22 | 238 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.5655 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 238
15 | 1411-JM001B | PMCC-1 | INSTRUMENT AIR COMPRESSOR- B | INSTRUMENT AIR COMPRESSOR AREA | B | MOTOR | 160 | kW | 3Ph | 400 | 0.86 | 0.964 | 278.5715 | 1671.4288 | 0.2 | 65 | 0 | 0 | AIR | 3C | 300 | 3C X 300 | 3C X 300+PE | 0.6/1.0 | 459 | 0.128 | 0.0711 | 28 | 157 | 22 | 8 | 22 | 237 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.0921 | YES | 8.1702 | YES | 2R x 0.6/1kV x 3C x 300 Sqmm | 2R x 0.6/1kV x 3C x 300+PE Sqmm | 474
16 | 1411-JM001B | PMCC-1 | INSTRUMENT AIR COMPRESSOR- B-SPACE HEATER | INSTRUMENT AIR COMPRESSOR AREA | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 28 | 157 | 22 | 8 | 22 | 237 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.5589 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 237
17 | 1411-JM001C | PMCC-1 | INSTRUMENT AIR COMPRESSOR- C | INSTRUMENT AIR COMPRESSOR AREA | A | MOTOR | 160 | kW | 3Ph | 400 | 0.86 | 0.964 | 278.5715 | 1671.4288 | 0.2 | 65 | 0 | 0 | AIR | 3C | 300 | 3C X 300 | 3C X 300+PE | 0.6/1.0 | 459 | 0.128 | 0.0711 | 29 | 157 | 22 | 8 | 22 | 238 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.1009 | YES | 8.2047 | YES | 2R x 0.6/1kV x 3C x 300 Sqmm | 2R x 0.6/1kV x 3C x 300+PE Sqmm | 476
18 | 1411-JM001C | PMCC-1 | INSTRUMENT AIR COMPRESSOR- C-SPACE HEATER | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 29 | 157 | 22 | 8 | 22 | 238 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.5655 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 238
19 | 1411-D001A | PMCC-1 | INSTRUMENT AIR DRYER | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.89376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.5018 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 256
20 | 1411-D001B | PMCC-1 | STANDBY INSTRUMENT AIR DRYER | INSTRUMENT AIR COMPRESSOR AREA | B | POWER | 0.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.89376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 28 | 162 | 22 | 8 | 22 | 242 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.47436 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 242
21 | 1411-V001 | PMCC-1 | ADT for Air receciver 25M³ | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.03 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.21658 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 28 | 162 | 22 | 8 | 22 | 242 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.17255 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 242
22 | 1411-V002A | PMCC-1 | ADT for Air receciver 60M³ | INSTRUMENT AIR COMPRESSOR AREA | B | POWER | 0.03 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.21658 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.18253 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 256
23 | 1411-V002B | PMCC-1 | ADT for Air receciver 60M³ | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.03 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.21658 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 28 | 162 | 22 | 8 | 22 | 242 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.17255 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 242
24 | 1417-P-001A | PMCC-1 | Electrolyte (KOH) Drain pump | INSTRUMENT AIR COMPRESSOR AREA | B | MOTOR | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 32.1753 | 0.2 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.019 | YES | 3.1257 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 256
25 | 1417-P-001B | PMCC-1 | Electrolyte (KOH) Drain pump | INSTRUMENT AIR COMPRESSOR AREA | B | MOTOR | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 32.1753 | 0.2 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.019 | YES | 3.1257 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 256
X | - | PMCC-1 | MASTER PLC | INSTRUMENT AIR COMPRESSOR AREA | B | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.0072 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 256
X |  |  | ASU PACKAGE (1404-PK001)
X | - | PMCC-1 | ASU-SELF CLEANING FILTER A | AIR SEPARATION UNIT | B | MOTOR | 0.1 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.23967 | 1.438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 103 | 22 | 8 | 17 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm
X | - | PMCC-1 | ASU-SELF CLEANING FILTER B | AIR SEPARATION UNIT | A | MOTOR | 0.1 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.23967 | 1.438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 40 | 103 | 22 | 8 | 18 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm
X | - | PMCC-1 | ASU-PRECOOLING SYSTEM A | AIR SEPARATION UNIT | B | MOTOR | 78 | kW | 3Ph | 400 | 0.85 | 0.957 | 138.4063 | 830.4378 | 0.2 | 65 | 0 | 0 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 33 | 133 | 22 | 8 | 20 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 150 Sqmm | 1R x 0.6/1kV x 3C x 150+PE Sqmm
X | - | PMCC-1 | ASU-PRECOOLING SYSTEM B | AIR SEPARATION UNIT | B | MOTOR | 78 | kW | 3Ph | 400 | 0.85 | 0.957 | 138.4063 | 830.4378 | 0.2 | 65 | 0 | 0 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 33 | 133 | 22 | 8 | 20 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 150 Sqmm | 1R x 0.6/1kV x 3C x 150+PE Sqmm
X | - | PMCC-1 | EXPANDER ELECTRIC HEATER | AIR SEPARATION UNIT | B | POWER | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 158 | 22 | 8 | 23 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm
STEAM TURBINE GENERATOR
26 | - | PMCC-1 | STG 1401-JT/JC301 - FEEDER (SPARE) | AMMONIA PLANT | B | POWER | 86.54 | kW | 3Ph | 400 | 0.85 | 0.95 | 154.6915 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 300 | 3.5C X 300 | 3.5C X 300 | 0.6/1.0 | 459 | 0.128 | 0.0711 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.165 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 884
27 | - | PMCC-1 | STG 1401-JT/JC301 - FEEDER (SPARE) | AMMONIA PLANT | A | POWER | 86.54 | kW | 3Ph | 400 | 0.85 | 0.95 | 154.6915 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 300 | 3.5C X 300 | 3.5C X 300 | 0.6/1.0 | 459 | 0.128 | 0.0711 | 29 | 335 | 38 | 8 | 41 | 451 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.2091 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 902
28 | 1401-P-1601 | PMCC-1 | Lubricating oil pump 1 | AMMONIA PLANT | A | MOTOR | 22 | kW | 3Ph | 400 | 0.85 | 0.95 | 39.3253 | 235.9519 | 0.2 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 28 | 335 | 38 | 8 | 41 | 450 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 2 | YES | 1.4834 | YES | 3.5383 | YES | 2R x 0.6/1kV x 3C x 95 Sqmm | 2R x 0.6/1kV x 3C x 95+PE Sqmm | 900
29 | - | PMCC-1 | Lubricating oil pump 1-Space Heater | AMMONIA PLANT | A | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 28 | 335 | 38 | 8 | 41 | 450 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.88798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 450
29 | 1401-P-1602 | PMCC-1 | Lubricating oil pump 2 | AMMONIA PLANT | B | MOTOR | 22 | kW | 3Ph | 400 | 0.85 | 0.95 | 39.3253 | 235.9519 | 0.2 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 2 | YES | 1.457 | YES | 3.4754 | YES | 2R x 0.6/1kV x 3C x 95 Sqmm | 2R x 0.6/1kV x 3C x 95+PE Sqmm | 884
30 | - | PMCC-1 | Lubricating oil pump 2-Space Heater | AMMONIA PLANT | B | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.87219 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 442
30 | - | PMCC-1 | Generator heater | AMMONIA PLANT | A | POWER | 0.4 | kW | 1Ph | 230 | 0.85 | 0.95 | 2.1537 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 335 | 38 | 8 | 41 | 451 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.4845 | YES | NA | NA | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6 Sqmm | 451
31 | 1401-PM-1604A | PMCC-1 | GSC Blower | AMMONIA PLANT | B | MOTOR | 3.7 | kW | 3Ph | 400 | 0.85 | 0.95 | 6.6138 | 39.6828 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.6797 | YES | 4.3128 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | 442
32 | 1401-PM-1604 | PMCC-1 | Oil Vapour Extractor | AMMONIA PLANT | A | MOTOR | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 16.0876 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 335 | 38 | 8 | 41 | 451 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.6521 | YES | 3.9988 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 451
33 | 1401-HT-1601 | PMCC-1 | Heater for oil tank | AMMONIA PLANT | B | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 335 | 38 | 8 | 41 | 437 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.4996 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 437
34 | 1401-PM112A | PMCC-1 | Condensate Extraction Pump 1 | AMMONIA PLANT | A | MOTOR | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 80.4382 | 0.2 | 65 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 335 | 38 | 8 | 41 | 451 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.5797 | YES | 4.7094 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 451
35 | 1401-PM112B | PMCC-1 | Condensate Extraction Pump 2 | AMMONIA PLANT | B | MOTOR | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 80.4382 | 0.2 | 65 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.5282 | YES | 4.6154 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 442
36 | - | PMCC-1 | Barring Gear Motor | AMMONIA PLANT | B | MOTOR | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 80.4382 | 0.2 | 65 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.5282 | YES | 4.6154 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 442
37 | - | PMCC-1 | GVC motor | AMMONIA PLANT | B | MOTOR | 5.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 9.8313 | 58.988 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.5439 | YES | 4.3799 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 442
Synthesis Gas compressor 1401-J-103
38 | 1401-HT103A | PMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J103 | AMMONIA PLANT | A | POWER | 17.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 31.2815 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 29 | 286 | 38 | 8 | 37 | 398 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.0872 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 398
39 | - | PMCC-1 | UCP FOR 1401-J103 (UPS 230 V)(REDUNDANT SUPPLY) | CENTRAL CONTROL BUILDING | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.95 | 26.9215 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4669 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 90
40 | - | PMCC-1 | UCP FOR 1401-J103 (UPS 230 V)(MAIN SUPPLY) | CENTRAL CONTROL BUILDING | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.95 | 26.9215 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4669 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 90
41 | - | PMCC-1 | LUBE OIL ELECTRIC HEATER B for 1401-J103 | AMMONIA PLANT | A | POWER | 17.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 31.2815 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 29 | 287 | 38 | 8 | 37 | 399 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.0925 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 399
42 | - | PMCC-1 | MOTOR SPACE HEATER FOR 1401-J103(230V) | AMMONIA PLANT | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 297 | 38 | 8 | 37 | 400 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1928 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 400
X | - | PMCC-1 | MISCLENEOUS LOADS FOR SPARES | AMMONIA PLANT | A | POWER | 55 | kW | 3Ph | 400 | 0.85 | 0.95 | 98.3133 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 296 | 38 | 8 | 38 | 409 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 2 | YES | 11.77 | NO | NA | NA | 2R x 0.6/1kV x 3.5C x 25 Sqmm | 2R x 0.6/1kV x 3.5C x 25 Sqmm | 818
X | - | PMCC-1 | LUBE OIL ELECTRIC HEATER B for 1401-J105 | AMMONIA PLANT | A | POWER | 17.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 31.2815 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 304 | 38 | 8 | 38 | 417 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 7.6365 | NO | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm
X | - | PMCC-1 | MOTOR SPACE HEATER FOR 1401-J105 | AMMONIA PLANT | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 25 | 4C X 25 | 4C X 25 | 0.6/1.0 | #N/A | #N/A | #N/A | 38 | 304 | 38 | 8 | 39 | 427 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A | #N/A | #N/A | #N/A | #N/A | NA | NA | #N/A | #N/A
43 | 0 | PMCC-1 | SPACE HEATER FOR SPARE LUBE OIL PUMP FOR 1401-J103 (230 V) | AMMONIA PLANT | A | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 286 | 38 | 8 | 37 | 398 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.13091 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 398
44 | 0 | PMCC-1 | SPACE HEATER FOR MAIN LUBE OIL PUMP FOR1401-J103 (230 V) | AMMONIA PLANT | B | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 287 | 38 | 8 | 36 | 389 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.12795 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 389
45 | 1401-CM113 | PMCC-1 | OIL DEMISTER FAN MOTOR FOR 1401-J103 | AMMONIA PLANT | A | MOTOR | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 42.9003 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 286 | 38 | 8 | 37 | 398 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.6086 | YES | 4.1984 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | 398
46 | 0 | PMCC-1 | UCP LIGHTNING FOR 1401-J103 (NON-UPS 230 V) | CENTRAL CONTROL BUILDING | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 125 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.68524 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 125
47 | 1401-CM106 | PMCC-1 | TURNING GEAR MOTOR FOR GEAR BOX | AMMONIA PLANT | A | MOTOR | 1.1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.9663 | 11.7976 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 297 | 38 | 8 | 38 | 410 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.7681 | YES | 2.6658 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 410
48 | 1401-HT105 | PMCC-1 | PRIMARY SEAL GAS HEATER (LP) | AIR SEPARATION UNIT | B | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 20 | 142 | 38 | 8 | 21 | 229 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.8061 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 229
49 | 1401-HT106 | PMCC-1 | PRIMARY SEAL GAS HEATER (MP) | AIR SEPARATION UNIT | A | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.9581 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 239
50 | 1401-HT107 | PMCC-1 | PRIMARY SEAL GAS HEATER (HP) | AIR SEPARATION UNIT | B | POWER | 8 | kW | 3Ph | 400 | 0.85 | 0.95 | 14.3001 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 142 | 38 | 8 | 21 | 229 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9171 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 229
51 | 0 | PMCC-1 | MAIN VFD AUX. POWER SUPPLY | AIR SEPARATION UNIT | A | POWER | 28 | kW | 3Ph | 400 | 0.85 | 0.95 | 50.0504 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.0054 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 239
X | - | PMCC-1 | LUBE OIL PURIFIER - SEPARATION CYLINDER MOTOR | AMMONIA PLANT | A | MOTOR | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 32.1753 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 286 | 38 | 8 | 37 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.28254 | YES | 0.48645 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 90
X | - | PMCC-1 | LUBE OIL PURIFIER - BOOSTER WATER PUMP | AMMONIA PLANT | B | MOTOR | 0.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.3406 | 8.0438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 286 | 38 | 8 | 36 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.070636 | YES | 0.12161 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 90
X | - | PMCC-1 | LUBE OIL PURIFIER - OIL SUPPLY PUMP | AMMONIA PLANT | A | MOTOR | 0.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.3406 | 8.0438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 286 | 38 | 8 | 37 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.070636 | YES | 0.12161 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 90
X | - | PMCC-1 | LUBE OIL PURIFIER - SLAG DISCHARGE PUMP | AMMONIA PLANT | B | MOTOR | 0.55 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.98313 | 5.8988 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 286 | 38 | 8 | 36 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.0518 | YES | 0.089183 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 90
X | - | PMCC-1 | LUBE OIL PURIFIER - ELECTRICAL PANEL | CENTRAL CONTROL BUILDING | A | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 25 | 4C X 25 | 4C X 25 | 0.6/1.0 | #N/A | #N/A | #N/A | 29 | 80 | 5 | 8 | 13 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A | #N/A | #N/A | #N/A | #N/A | NA | NA | #N/A | #N/A | #N/A
X | - | PMCC-1 | LUBE OIL PURIFIER - PLC PANEL | CENTRAL CONTROL BUILDING | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 25 | 4C X 25 | 4C X 25 | 0.6/1.0 | #N/A | #N/A | #N/A | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A | #N/A | #N/A | #N/A | #N/A | NA | NA | #N/A | #N/A | #N/A
AMMONIA REFRIGERATION COMPRESSOR 1401-J-105
52 | 1401-HT105A | PMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J105 | AMMONIA PLANT | A | POWER | 13 | kW | 3Ph | 400 | 0.85 | 0.95 | 23.2377 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 304 | 38 | 8 | 38 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.2244 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 90
53 | - | PMCC-1 | UCP FOR 1401-J105 (UPS 230 V)(REDUNDANT SUPPLY) | CENTRAL CONTROL BUILDING | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.95 | 26.9215 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4669 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 90
54 | - | PMCC-1 | UCP FOR 1401-J105 (UPS 230 V)(MAIN SUPPLY) | CENTRAL CONTROL BUILDING | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.95 | 26.9215 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4669 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 90
55 | - | PMCC-1 | UCP LIGHTNING FOR 1401-J105 (NON-UPS 230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.8592 | YES | NA | NA | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6 Sqmm | 135
56 | 1401-HT105B | PMCC-1 | LUBE OIL ELECTRIC HEATER B for 1401-J105 | AMMONIA PLANT | B | POWER | 13 | kW | 3Ph | 400 | 0.85 | 0.95 | 23.2377 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 20 | 304 | 38 | 8 | 37 | 407 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 2.136 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 407
57 | 1401-HT206 | PMCC-1 | MOTOR SPACE HEATER FOR 1401-J105 (230 V) | AMMONIA PLANT | A | POWER | 0.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3074 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 314 | 38 | 8 | 39 | 428 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.877 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 428
58 | 1401-CM107 | PMCC-1 | TURNING GEAR MOTOR FOR GEAR BOX | AMMONIA PLANT | B | MOTOR | 1.1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.9663 | 11.7976 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 309 | 38 | 8 | 38 | 413 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.781 | YES | 2.6853 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 413
59 | 1401-HT207 | PMCC-1 | PRIMARY SEAL GAS HEATER (LP) | AIR SEPARATION UNIT | A | POWER | 6 | kW | 3Ph | 400 | 0.85 | 0.95 | 10.7251 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.5006 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 239
60 | 1401-HT108 | PMCC-1 | PRIMARY SEAL GAS HEATER (HP) | AIR SEPARATION UNIT | B | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 20 | 142 | 38 | 8 | 21 | 229 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.8061 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 229
61 | - | PMCC-1 | MAIN VFD AUX. POWER SUPPLY | AIR SEPARATION UNIT | A | POWER | 16 | kW | 3Ph | 400 | 0.85 | 0.95 | 28.6002 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.1865 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 239
62 | 1401-PM107 | PMCC-1 | LUBE OIL CONDITIONER OIL PUMP MOTOR | AIR SEPARATION UNIT | A | MOTOR | 5.25 | kW | 3Ph | 400 | 0.85 | 0.95 | 9.3845 | 56.3067 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.056 | YES | 3.309 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | 239
N2 Compressor
62 | - | PMCC-1 | SPACE HEATER FOR 1401-CM201 (230V) | AMMONIA PLANT | A | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 283 | 38 | 8 | 36 | 394 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1599 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 394
63 | 1401-DM210 | PMCC-1 | OIL MIST ELIMINATOR MOTOR FOR 1401-J201 | AMMONIA PLANT | B | MOTOR | 0.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.3406 | 8.0438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 284 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.132 | YES | 1.7068 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 385
64 | 1401-PKM210A | PMCC-1 | NOISE ENCLOSURE FANS MOTOR FOR 1401-J201 | AMMONIA PLANT | A | MOTOR | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 16.0876 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 285 | 38 | 8 | 36 | 396 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.3287 | YES | 3.5111 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 396
65 | 1401-PKM210B | PMCC-1 | NOISE ENCLOSURE FANS MOTOR FOR 1401-J201 | AMMONIA PLANT | B | MOTOR | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 16.0876 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 285 | 38 | 8 | 36 | 387 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.2757 | YES | 3.4313 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 387
66 | 1401-B210 | PMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J201 | AMMONIA PLANT | A | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 287 | 38 | 8 | 37 | 399 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.5642 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 399
67 | 1401-B211 | PMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J201 | AMMONIA PLANT | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 287 | 38 | 8 | 36 | 389 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.525 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 389
68 | 401-PJB-1401 | PMCC-1 | Acoustic Enclosure lighting JB (230V) (NON-UPS Supply) | CENTRAL CONTROL BUILDING | B | POWER | 0.6 | kW | 1Ph | 230 | 0.85 | 0.95 | 3.2306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 85 | 10 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.6758 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 136
69 | 401-PLC-1401 | PMCC-1 | Package PLC Panel (230V)(NON-UPS Supply) | CENTRAL CONTROL BUILDING | B | POWER | 0.9 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.8459 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 20 | 85 | 10 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.6857 | YES | NA | NA | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6 Sqmm | 136
70 | 401-MMS-1401 | PMCC-1 | MMS Panel (230V) (NON-UPS Supply) | CENTRAL CONTROL BUILDING | A | POWER | 1.1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.9227 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 85 | 10 | 8 | 14 | 146 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.2118 | YES | NA | NA | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6 Sqmm | 146
71 | 401-PLC-1401 | PMCC-1 | Package PLC Panel (UPS supply) (230V) | CENTRAL CONTROL BUILDING | B | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 85 | 10 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.1013 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 136
72 | 401-MMS-1401 | PMCC-1 | MMS Panel (UPS supply) (230V) | CENTRAL CONTROL BUILDING | A | POWER | 2.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 11.8455 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 85 | 10 | 8 | 14 | 146 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.7608 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 146
73 | - | PMCC-1 | Laptop (UPS supply) (230V) | CENTRAL CONTROL BUILDING | B | POWER | 0.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 2.6922 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 85 | 10 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.3965 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 136
Auxiliary H2 Compressor (1401-J-202A/B)
X | - | PMCC-1 | UCP CABINET FOR 1401-J203A | AMMONIA PLANT | B | MOTOR | 6 | kW | 3Ph | 400 | 0.82 | 0.896 | 11.7875 | 70.725 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 237 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm
X | - | PMCC-1 | REMOTE I/O CABINET FOR 1401-J203A | AMMONIA PLANT | A | MOTOR | 4 | kW | 3Ph | 400 | 0.79 | 0.886 | 8.2488 | 49.4929 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm
X | - | PMCC-1 | MMS CABINET FOR 1401-J203A | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.75 | 0.853 | 4.5124 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm
X | - | PMCC-1 | UCP CABINET FOR 1401-J203B | AMMONIA PLANT | B | POWER | 6 | kW | 3Ph | 400 | 0.85 | 0.95 | 10.7251 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm
X | - | PMCC-1 | REMOTE I/O CABINET FOR1401-J203B | AMMONIA PLANT | B | MOTOR | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 42.9003 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm
X | - | PMCC-1 | MMS CABINET FOR 1401-J203B | AMMONIA PLANT | B | POWER | 1.6 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.86 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm
74 | 1401-H202A | PMCC-1 | FRAME OIL HEATER FOR 1401-J202A | AMMONIA PLANT | A | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 237 | 38 | 8 | 32 | 344 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.9677 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 344
75 | - | PMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J202A (240 V) | AMMONIA PLANT | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 267 | 38 | 8 | 34 | 367 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.0119 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 367
76 | - | PMCC-1 | Excitation Panel Main supply | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 269 | 38 | 8 | 35 | 379 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.9928 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 379
77 | - | PMCC-1 | Excitation Panel Aux supply (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
78 | - | PMCC-1 | Excitation Panel Aux supply (UPS) (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
79 | - | PMCC-1 | Excitation Panel control supply (24 VDC / 110 VDC) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
80 | 1401-H202B | PMCC-1 | FRAME OIL HEATER FOR 1401-J202B | AMMONIA PLANT | A | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 269 | 38 | 8 | 35 | 379 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.1679 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 379
81 | - | PMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J202B (240 V) | AMMONIA PLANT | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 270 | 38 | 8 | 34 | 370 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.0283 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 370
82 | - | PMCC-1 | Excitation Panel Main supply | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 269 | 38 | 8 | 35 | 379 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.9928 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 379
83 | - | PMCC-1 | Excitation Panel Aux supply (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
84 | - | PMCC-1 | Excitation Panel Aux supply (UPS) (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
85 | - | PMCC-1 | Excitation Panel control supply (24 VDC / 110 VDC) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
|  |  | Auxiliary H2 Compressor (1401-J-203A/B) | [16 empty] | 3C
86 | 1401-H203A | PMCC-1 | FRAME OIL HEATER FOR 1401-J203A | AMMONIA PLANT | A | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 247 | 38 | 8 | 33 | 355 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.0306 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 355
87 | - | PMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J203A (240 V) | AMMONIA PLANT | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 256 | 38 | 8 | 33 | 355 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9461 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 355
88 | - | PMCC-1 | Excitation Panel Main supply | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 257 | 38 | 8 | 34 | 366 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.9244 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 366
89 | - | PMCC-1 | Excitation Panel Aux supply (240 V) | CENTRAL CONTROL BUILDING | B | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 80 | 5 | 8 | 12 | 125 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.1459 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 125
90 | - | PMCC-1 | Excitation Panel Aux supply (UPS) (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
91 | - | PMCC-1 | Excitation Panel control supply (24 VDC / 110 VDC) | CENTRAL CONTROL BUILDING | B | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 80 | 5 | 8 | 12 | 125 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.1459 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 125
92 | 1401-B203C | PMCC-1 | WATER TANK HEATER FOR 1401-J203A/B & 1401-J202A/B | AMMONIA PLANT | A | POWER | 70 | kW | 3Ph | 400 | 0.85 | 0.95 | 125.126 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 29 | 247 | 38 | 8 | 33 | 350 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 2.4933 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 700
93 | 1401-H203B | PMCC-1 | FRAME OIL HEATER FOR 1401-J203A | AMMONIA PLANT | B | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 248 | 38 | 8 | 32 | 346 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.9791 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 346
94 | - | PMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J203 B (240 V) | AMMONIA PLANT | A | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 262 | 38 | 8 | 34 | 371 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.0338 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 371
95 | - | PMCC-1 | Excitation Panel Main supply | AMMONIA PLANT | B | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 263 | 38 | 8 | 33 | 362 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.1863 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 362
96 | - | PMCC-1 | Excitation Panel Aux supply (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
97 | - | PMCC-1 | Excitation Panel Aux supply (UPS) (240 V) | CENTRAL CONTROL BUILDING | B | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
98 | - | PMCC-1 | Excitation Panel control supply (24 VDC / 110 VDC) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135
Other Load
99 | 1421-MLDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR MLDB-1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 85 | kW | 3Ph | 400 | 0.85 | 0.95 | 151.9387 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 34 | 0 | 5 | 8 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 0.89963 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 52
100 | 1421-MLDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR MLDB-1 / FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 85 | kW | 3Ph | 400 | 0.85 | 0.95 | 151.9387 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 18 | 0 | 5 | 8 | 4 | 35 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 0.60552 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 35
101 | 1421-WDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR WDB-1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 60 | kW | 3Ph | 400 | 0.85 | 0.95 | 107.2509 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 34 | 0 | 5 | 8 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 0.93498 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 52
102 | 1421-PDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR PDB-1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 363.56 | kW | 3Ph | 400 | 0.85 | 0.951 | 649.1854 | 0 | 0.00 | 65 | 0 | 0 | AIR | 1C | 500 | 1C X 500 | 1C X 500 | 0.6/1.0 | 704 | 0.0774 | 0.0851 | 32 | 0 | 5 | 8 | 5 | 50 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 507.5136 | 2 | YES | 0.77739 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 500 Sqmm/Phase | 2R x 0.6/1.0kV x 1C x 500 Sqmm/Phase | 400
103 | 1421-PDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR PDB-1 / FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 363.56 | kW | 3Ph | 400 | 0.85 | 0.951 | 649.1854 | 0 | 0.00 | 65 | 0 | 0 | AIR | 1C | 500 | 1C X 500 | 1C X 500 | 0.6/1.0 | 704 | 0.0774 | 0.0851 | 16 | 0 | 5 | 8 | 3 | 32 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 507.5136 | 2 | YES | 0.49753 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 500 Sqmm/Phase | 2R x 0.6/1.0kV x 1C x 500 Sqmm/Phase | 256
104 | 1421-ESWG-4-0001 | PMCC-1 | OUTGOING FEEDER FOR EPMCC - 1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 5 | YES | 0.76256 | YES | NA | NA | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 555
105 | 1421-ESWG-4-0001 | PMCC-1 | OUTGOING FEEDER FOR EPMCC - 1 / FEEDER-1 (Neutral) | MAIN SUBSTATION BUILDING | A | POWER | 923.7875 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 1436.3645 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 3 | YES | 0.73379 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 630 Sqmm | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 111
106 | 1421-ESWG-4-0001 | PMCC-1 | OUTGOING FEEDER FOR EPMCC - 1 / FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 5 | YES | 0.76256 | YES | NA | NA | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 555
107 | 1421-ESWG-4-0001 | PMCC-1 | OUTGOING FEEDER FOR EPMCC - 1 / FEEDER-2 (Neutral) | MAIN SUBSTATION BUILDING | B | POWER | 923.7875 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 1436.3645 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 3 | YES | 0.73379 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 630 Sqmm | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 111
108 | 1421-ESWG-4-0001 | EDG | EPMCC-1 (INCOMER-3 - DG) | MAIN SUBSTATION BUILDING |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 33 | 7 | 10 | 8 | 6 | 64 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 5 | YES | 1.319 | YES | NA | NA | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 960
109 | 1421-ESWG-4-0001 | EDG | EPMCC-1 (INCOMER-3 - DG Neutral) | MAIN SUBSTATION BUILDING |  | INCOMER | 923.7875 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 1436.3645 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 33 | 7 | 10 | 8 | 6 | 64 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 3 | YES | 1.2693 | YES | NA | NA | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 192
110 | - | PMCC-1 | CRANE - Ammonia plant (Hydrogen Compressor: 1401- J202A, shed) - Double Girder EOT Crane - (20T) | Ammonia plant (Hydrogen Compressor: 1401- J202A, shed) | A | MOTOR | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 268.1272 | 0.2 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 29 | 275 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.8844 | YES | 6.88 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 385
111 | - | PMCC-1 | CRANE - Ammonia plant (Hydrogen Compressor: 1401- J202A, shed) - Double Girder EOT Crane - (20T)-Space Heater | Ammonia plant (Hydrogen Compressor: 1401- J202A, shed) | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 275 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.5813 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 385
111 | - | PMCC-1 | CRANE- Ammonia plant (Hydrogen Compressor: 1401- J203A, shed) - Double Girder EOT Crane - (20T) | Ammonia plant (Hydrogen Compressor: 1401- J203A, shed) | B | MOTOR | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 268.1272 | 0.2 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 20 | 275 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.8169 | YES | 6.7192 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 376
112 | - | PMCC-1 | CRANE- Ammonia plant (Hydrogen Compressor: 1401- J203A, shed) - Double Girder EOT Crane - (20T)-Space Heater | Ammonia plant (Hydrogen Compressor: 1401- J203A, shed) | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 20 | 275 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 2.4732 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 376
112 | - | PMCC-1 | Electric Hoist - Main substation building (Switchgear room) - Electric Hoist (2T) | Main Sub station building Switch gear Room | A | MOTOR | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 53.6254 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 0 | 5 | 8 | 5 | 47 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.92127 | YES | 1.3891 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 47 | Size changed to 25 to 4sqmm
113 | - | PMCC-1 | Electric Hoist - Instrument air compressor building) - Electric Hoist (5T) | Instrument air compressor building) | B | MOTOR | 8 | kW | 3Ph | 400 | 0.85 | 0.95 | 14.3001 | 85.8007 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 168 | 38 | 8 | 24 | 258 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1599 | YES | 3.7187 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 258
114 | - | PMCC-1 | CRANE- Air Separation unit - Single Girder EOT Crane - (8T) | Air Seperation unit | B | MOTOR | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 160.8763 | 0.2 | 65 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.7341 | YES | 4.9913 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 239
114 | 1421-SWG-4-0001 | PMCC-1 | PMCC-1(INCOMER 1) | MAIN SUBSTATION BUILDING |  | INCOMER | 3150 | kVA | 3Ph | 400 | 0.85043 | 0.91225 | 4984.1355 | LV BUSDUCT-400V
115 | 1421-SWG-4-0001 | PMCC-1 | PMCC-1 (INCOMER 2) | MAIN SUBSTATION BUILDING |  | INCOMER | 3150 | kVA | 3Ph | 400 | 0.85043 | 0.91225 | 4984.1355 | LV BUSDUCT-400V
ASU PACKAGE DISTRIBUTION TRANSFORMER TO MCC PANEL
116 | 1421-ESWG-4-0001 | ASU package Transformer | ASU MCC Panel | AIR SEPARATION UNIT | B | POWER | 700 | kW | 3Ph | 400 | 0.84665 | 0.92832 | 1285.5453 | 0 | 0.00 | 50 | 1 | 349.6503 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 10 | 0 | 5 | 8 | 3 | 26 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 3 | YES | 0.4615 | YES | NA | NA | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 234
117 | 1421-ESWG-4-0001 | ASU package Transformer | ASU MCC Panel Neutral | AIR SEPARATION UNIT | B | POWER | 404.157 | kW | 3Ph | 400 | 0.84665 | 0.92832 | 742.2317 | 0 | 0.00 | 50 | 1 | 349.6503 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 10 | 0 | 5 | 8 | 3 | 26 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 2 | YES | 0.39968 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 630 Sqmm | 2R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 52
EPMCC-1
118 | 1400-P001A | EPMCC-1 | DIESEL OFFLOADING PUMP | Diesel storage area | A | MOTOR | 11 | kW | 3Ph | 400 | 0.75 | 0.853 | 24.8184 | 148.9107 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 152 | 10 | 8 | 21 | 229 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.9753 | YES | 5.7285 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 229
119 | 1400-P001B | EPMCC-1 | SPARE DIESEL OFFLOADING PUMP | Diesel storage area | B | MOTOR | 11 | kW | 3Ph | 400 | 0.75 | 0.853 | 24.8184 | 148.9107 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 30 | 162 | 10 | 8 | 21 | 230 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.9883 | YES | 5.7535 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 230
120 | 1401-PM124A | EPMCC-1 | COLD AMMONIA PRODUCT PUMP | AMMONIA PLANT | A | MOTOR | 22 | kW | 3Ph | 400 | 0.84 | 0.927 | 40.7808 | 244.6848 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 38 | 317 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.9989 | YES | 7.208 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 442 | initially 120sqmm with 322.5 mtr length ,now 95 sqm with 317 mtr
121 |  | EPMCC-1 | SPACE HEATER COLD AMMONIA PRODUCT PUMP | AMMONIA PLANT | A | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 38 | 322.5 | 38 | 8 | 41 | 447.5 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.88305 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 447.5
122 | 1401-PM124B | EPMCC-1 | SPARE COLD AMMONIA PRODUCT PUMP | AMMONIA PLANT | B | MOTOR | 22 | kW | 3Ph | 400 | 0.84 | 0.927 | 40.7808 | 244.6848 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 322.5 | 38 | 8 | 40 | 438.5 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.9752 | YES | 7.151 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 438.5
123 |  | EPMCC-1 | SPACE HEATER SPARE COLD AMMONIA PRODUCT PUMP | AMMONIA PLANT | B | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 30 | 322.5 | 38 | 8 | 40 | 438.5 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.86529 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 438.5
124 | 1401-PM104A | EPMCC-1 | BFW PUMP | AMMONIA PLANT | A | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.95 | 134.0636 | 804.3816 | 0.2 | 65 | 0 | 0 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 38 | 257 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 2.8699 | YES | 8.1539 | YES | 2R x 0.6/1kV x 3C x 150 Sqmm | 2R x 0.6/1kV x 3C x 150+PE Sqmm | 752
125 |  | EPMCC-1 | SPACE HEATER BFW PUMP | AMMONIA PLANT | A | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 38 | 257 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.74196 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 376
126 | 1401-PM104B | EPMCC-1 | SPARE BFW PUMP | AMMONIA PLANT | B | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.95 | 134.0636 | 804.3816 | 0.2 | 65 | 0 | 0 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 30 | 258 | 38 | 8 | 34 | 368 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 2.8088 | YES | 7.9804 | YES | 2R x 0.6/1kV x 3C x 150 Sqmm | 2R x 0.6/1kV x 3C x 150+PE Sqmm | 736
127 |  | EPMCC-1 | SPACE HEATER SPARE BFW PUMP | AMMONIA PLANT | B | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 30 | 258 | 38 | 8 | 34 | 368 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.72617 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 368
Ammonia Storage
128 | 1402-PK007 | EPMCC-1 | LP FLARE PACKAGE | AMMONIA STORAGE AREA | B | POWER | 0.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.89376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 424 | 38 | 8 | 50 | 549 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.0761 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 549
129 | 1402-B001-TCP01 | EPMCC-1 | HEATER CONTROL PANEL (400V/230V) | AMMONIA STORAGE AREA | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 362 | 38 | 8 | 44 | 481 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8857 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 481
130 | 1402-PK007 -CP01 | EPMCC-1 | IGNITION PANEL (400V/230V) | AMMONIA STORAGE AREA | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 362 | 38 | 8 | 44 | 481 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8857 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 481
131 | 1402-PK007 -CP02 | EPMCC-1 | WINCH CONTROL PANEL (400V/230V) | AMMONIA STORAGE AREA | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 362 | 38 | 8 | 44 | 481 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8857 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 481
132 | 1402-PK007 -CP03 | EPMCC-1 | AVIATION CONTROL PANEL (400V/230V) | AMMONIA STORAGE AREA | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 362 | 38 | 8 | 44 | 481 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8857 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 481
133 | 1402-PK006 | EPMCC-1 | HP FLARE PACKAGE | AMMONIA PLANT | A | POWER | 2.3 | kW | 1Ph | 230 | 0.85 | 0.95 | 12.3839 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 38 | 503 | 38 | 8 | 59 | 646 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.3325 | YES | NA | NA | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95 Sqmm | 646
STEAM TURBINE GENERATOR
134 | 1401-P-1603 | EPMCC-1 | Emergency oil pump (110V) | AMMONIA PLANT | A | POWER | 2.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 11.8455 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 38 | 335 | 38 | 8 | 42 | 461 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 2.1448 | YES | NA | NA | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70 Sqmm | 461
135 | - | EPMCC-1 | Monitoring cabinets (230V/110V) | AMMONIA PLANT | A | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 8.0765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 335 | 38 | 8 | 42 | 461 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.0713 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 461
X |  |  | ASU PACKAGE
X | - | EPMCC-1 | ASU-EXPANDER OIL SUPPLY PUMP A | AIR SEPARATION UNIT | A | MOTOR | 5 | kW | 3Ph | 400 | 0.82 | 0.896 | 9.8229 | 58.9375 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 35 | 123 | 22 | 8 | 19 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm
X | - | EPMCC-1 | ASU-EXPANDER OIL SUPPLY PUMP B | AIR SEPARATION UNIT | B | MOTOR | 5 | kW | 3Ph | 400 | 0.82 | 0.896 | 9.8229 | 58.9375 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 123 | 22 | 8 | 19 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm
X | - | EPMCC-1 | ASU-CONTROL SYSTEM | AIR SEPARATION UNIT | A | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 35 | 163 | 22 | 8 | 23 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm
Synthesis Gas compressor 1401-J-103
136 | 1401-PM103B | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J103 | AMMONIA PLANT | A | MOTOR | 37 | kW | 3Ph | 400 | 0.85 | 0.952 | 65.9991 | 395.9946 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 38 | 289 | 38 | 8 | 38 | 411 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 2 | YES | 2.2738 | YES | 5.4236 | YES | 2R x 0.6/1kV x 3C x 95 Sqmm | 2R x 0.6/1kV x 3C x 95+PE Sqmm | 822
137 | - | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J103-SPACE HEATER | AMMONIA PLANT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 38 | 289 | 38 | 8 | 38 | 411 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 2 | YES | 1.3517 | YES | NA | NA | 2R x 0.6/1kV x 3C x 2.5 Sqmm | 2R x 0.6/1kV x 3C x 2.5 Sqmm | 822
138 | 1401-PM103A | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J103 | AMMONIA PLANT | B | MOTOR | 37 | kW | 3Ph | 400 | 0.85 | 0.952 | 65.9991 | 395.9946 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 30 | 289 | 38 | 8 | 37 | 402 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 2.996 | YES | 6.4478 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 804
139 | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J103-SPACE HEATER | AMMONIA PLANT | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 30 | 289 | 38 | 8 | 37 | 402 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 2 | YES | 1.3221 | YES | NA | NA | 2R x 0.6/1kV x 3C x 2.5 Sqmm | 2R x 0.6/1kV x 3C x 2.5 Sqmm | 804
X | - | EPMCC-1 | OIL DEMISTER FAN MOTOR FOR 1401-J103 | AMMONIA PLANT | A | MOTOR | 2.2 | kW | 3Ph | 400 | 0.8 | 0.867 | 4.5783 | 27.4699 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 35 | 290 | 38 | 8 | 38 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm
X | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J105 | AMMONIA PLANT | B | MOTOR | 22 | kW | 3Ph | 400 | 0.82 | 0.933 | 41.5068 | 249.0408 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 304 | 38 | 8 | 38 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm
X | - | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J105 | AMMONIA PLANT | A | MOTOR | 22 | kW | 3Ph | 400 | 0.82 | 0.933 | 41.5068 | 249.0408 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 304 | 38 | 8 | 39 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm
X | - | EPMCC-1 | OIL DEMISTER FAN MOTOR FOR 1401-J105 | AMMONIA PLANT | B | MOTOR | 2.2 | kW | 3Ph | 400 | 0.8 | 0.867 | 4.5783 | 27.4699 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 304 | 38 | 8 | 38 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm
X | - | EPMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J105 | AMMONIA PLANT | A | POWER | 17.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 31.2815 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 35 | 304 | 38 | 8 | 39 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm
X | - | EPMCC-1 | UCP FANS & LIGHTNING FOR 1401-J105 | AMMONIA PLANT | B | POWER | 3.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 6.2563 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 304 | 38 | 8 | 38 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm
Synthesis Gas compressor 1401-J-105
140 | 1401-PM105A | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J105 | AMMONIA PLANT | A | MOTOR | 22 | kW | 3Ph | 400 | 0.82 | 0.933 | 41.5068 | 249.0408 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 38 | 304 | 38 | 8 | 39 | 427 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.9026 | YES | 7.0874 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 427
141 |  | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J105-SPACE HEATER | AMMONIA PLANT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 304 | 38 | 8 | 39 | 427 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.7538 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 427
142 | 1401-PM105B | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J105 | AMMONIA PLANT | B | MOTOR | 22 | kW | 3Ph | 400 | 0.82 | 0.933 | 41.5068 | 249.0408 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 304 | 38 | 8 | 38 | 418 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.8414 | YES | 6.938 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 418
143 |  | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J105-SPACE HEATER | AMMONIA PLANT | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 304 | 38 | 8 | 38 | 418 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.7169 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 418
144 | 1401-CM115 | EPMCC-1 | OIL DEMISTER FAN MOTOR FOR 1401-J105 | AMMONIA PLANT | A | MOTOR | 2.2 | kW | 3Ph | 400 | 0.8 | 0.867 | 4.5783 | 27.4699 | 0.2 | 50 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 38 | 304 | 38 | 8 | 39 | 427 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.714 | YES | 4.4512 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 427
N2 Compressor
145 | - | EPMCC-1 | AUXILIARY LUBE OIL PUMP FOR 1401-J201 | AMMONIA PLANT | A | MOTOR | 3.7 | kW | 3Ph | 400 | 0.82 | 0.896 | 7.269 | 43.6137 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 289 | 38 | 8 | 38 | 411 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.6487 | YES | 4.4076 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | 411
X | - | EPMCC-1 | MIST ELIMINATOR MOTOR FOR 1401-J201 | AMMONIA PLANT | B | MOTOR | 1.5 | kW | 3Ph | 400 | 0.75 | 0.853 | 3.3843 | 20.306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 270 | 38 | 8 | 35 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm
X | - | EPMCC-1 | NOISE ENCLOSURE FANS MOTOR FOR 1401-J201 | AMMONIA PLANT | A | MOTOR | 1.1 | kW | 3Ph | 400 | 0.8 | 0.841 | 2.3599 | 14.1596 | 0.2 | 50 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 35 | 270 | 38 | 8 | 36 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm
X | - | EPMCC-1 | NOISE ENCLOSURE FANS MOTOR FOR 1401-J201 | AMMONIA PLANT | B | MOTOR | 1.1 | kW | 3Ph | 400 | 0.8 | 0.841 | 2.3599 | 14.1596 | 0.2 | 50 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 270 | 38 | 8 | 35 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm
X | - | EPMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J201 | AMMONIA PLANT | A | POWER | 4.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.0438 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 35 | 270 | 38 | 8 | 36 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm
X | - | EPMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J201 | AMMONIA PLANT | B | POWER | 4.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.0438 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 270 | 38 | 8 | 35 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm
X | - | EPMCC-1 | PLC PANEL (01 Qty),PLC PANEL UTILITIES (FANS,LIGHTS,SOCKETS-01Qty),LOCAL CONTROL PANEL (01 Qty) FOR 1401-J201 | AMMONIA PLANT | A | POWER | 2.2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.9325 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 35 | 270 | 38 | 8 | 36 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm
Auxiliary H2 Compressor (1401-J-202A/B)
X | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J202A | AMMONIA PLANT | A | MOTOR | 15 | kW | 3Ph | 400 | 0.84 | 0.927 | 27.8051 | 166.8306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70+PE Sqmm
146 | 1401-P202C | EPMCC-1 | AUX. LUBE OIL PUMP FOR 1401-J202A | AMMONIA PLANT | B | MOTOR | 9.3 | kW | 3Ph | 400 | 0.84 | 0.927 | 17.2392 | 103.4349 | 0.2 | 50 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 30 | 237 | 38 | 8 | 32 | 345 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.5122 | YES | 4.6325 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 345
X | - | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J202A | AMMONIA PLANT | A | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm
X | - | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J202A | AMMONIA PLANT | B | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm
147 | 1401-BM202A | EPMCC-1 | BARRING DEVICE MOTOTR FOR 1401-J202A | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.79 | 0.886 | 11.3421 | 68.0527 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4137 | YES | 4.4356 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 388
X | - | EPMCC-1 | FRAME OIL HEATER FOR 1401-J202A | AMMONIA PLANT | A | POWER | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 120 | 3.5C X 120 | 3.5C X 120 | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 1R x 0.6/1kV x 3.5C x 120 Sqmm
X | - | EPMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J202A | AMMONIA PLANT | B | POWER | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm
X | - | EPMCC-1 | WATER TANK HEATER FOR 1401-J202A | AMMONIA PLANT | B | POWER | 40 | kW | 3Ph | 400 | 0.85 | 0.95 | 71.5006 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 185 | 3.5C X 185 | 3.5C X 185 | 0.6/1.0 | 338 | 0.21 | 0.0727 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 185 Sqmm | 1R x 0.6/1kV x 3.5C x 185 Sqmm
148 | - | EPMCC-1 | UCP CABINET (NON-UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.45 | kW | 1Ph | 230 | 0.85 | 0.95 | 7.8072 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.8047 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145
X | - | EPMCC-1 | REMOTE I/O CABINET FOR 1401-J202A | AMMONIA PLANT | B | POWER | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm
X | - | EPMCC-1 | MMS CABINET FOR1401-J202A | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm
X | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J202B | AMMONIA PLANT | B | MOTOR | 15 | kW | 3Ph | 400 | 0.84 | 0.927 | 27.8051 | 166.8306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70+PE Sqmm
149 | 1401-P202D | EPMCC-1 | AUX. LUBE OIL PUMP FOR 1401-J202B | AMMONIA PLANT | A | MOTOR | 9.3 | kW | 3Ph | 400 | 0.84 | 0.927 | 17.2392 | 103.4349 | 0.2 | 50 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 38 | 269 | 38 | 8 | 36 | 389 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.8326 | YES | 5.2233 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 389
X | - | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J202B | AMMONIA PLANT | B | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm
X | - | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J202B | AMMONIA PLANT | A | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm
150 | 1401-BM202B | EPMCC-1 | BARRING DEVICE MOTOTR FOR 1401-J202B | AMMONIA PLANT | B | MOTOR | 5.5 | kW | 3Ph | 400 | 0.79 | 0.886 | 11.3421 | 68.0527 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 33 | 271 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.395 | YES | 4.4013 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 385
X | - | EPMCC-1 | FRAME OIL HEATER FOR 1401-J202B | AMMONIA PLANT | A | POWER | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 120 | 3.5C X 120 | 3.5C X 120 | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 1R x 0.6/1kV x 3.5C x 120 Sqmm
X | - | EPMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J202B | AMMONIA PLANT | B | POWER | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm
X | - | EPMCC-1 | WATER TANK HEATER FOR 1401-J202B | AMMONIA PLANT | A | POWER | 40 | kW | 3Ph | 400 | 0.85 | 0.95 | 71.5006 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 240 | 3.5C X 240 | 3.5C X 240 | 0.6/1.0 | 401 | 0.16 | 0.0719 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 240 Sqmm | 1R x 0.6/1kV x 3.5C x 240 Sqmm
151 | - | EPMCC-1 | UCP CABINET (NON-UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | B | POWER | 1.45 | kW | 1Ph | 230 | 0.85 | 0.95 | 7.8072 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 80 | 5 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6927 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 136
X | - | EPMCC-1 | REMOTE I/O CABINET FOR 1401-J202B | AMMONIA PLANT | A | POWER | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm
X | - | EPMCC-1 | MMS CABINET FOR 1401-J202B | AMMONIA PLANT | B | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm
152 | 1401-PM202G | EPMCC-1 | HPU system motor | AMMONIA PLANT | A | POWER | 22 | kW | 3Ph | 400 | 0.85 | 0.95 | 39.3253 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 2 | YES | 2.4404 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 776
153 |  | EPMCC-1 | UCP CABINET (REDUNDANT UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2403 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145
154 |  | EPMCC-1 | ISC PANEL (NON-UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.18 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.96917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.53601 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145
155 |  | EPMCC-1 | ISC PANEL (REDUNDANT UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.81 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3613 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.412 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145
156 | 1401-PM202H | EPMCC-1 | HPU system motor | AMMONIA PLANT | A | POWER | 22 | kW | 3Ph | 400 | 0.85 | 0.95 | 39.3253 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 2 | YES | 2.4404 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 776
157 |  | EPMCC-1 | UCP CABINET (REDUNDANT UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2403 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145
158 |  | EPMCC-1 | ISC PANEL (NON-UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.18 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.96917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.53601 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145
159 |  | EPMCC-1 | ISC PANEL (REDUNDANT UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.81 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3613 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.412 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145
Auxiliary H2 Compressor (1401-J-203B)
160 | 1401-P203C | EPMCC-1 | AUX. LUBE OIL PUMP FOR 1401-J203A | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.84 | 0.927 | 10.1952 | 61.1712 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 247 | 38 | 8 | 34 | 365 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1558 | YES | 3.7507 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 365
X | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J203A | AMMONIA PLANT | B | MOTOR | 15 | kW | 3Ph | 400 | 0.84 | 0.927 | 27.8051 | 166.8306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70+PE Sqmm
161 | 1401-P203E | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J203A/B & 1401-J202A/B | AMMONIA PLANT | A | MOTOR | 30 | kW | 3Ph | 400 | 0.85 | 0.954 | 53.4006 | 320.4036 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 38 | 247 | 38 | 8 | 34 | 365 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 2.201 | YES | 4.7369 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 730
162 | - | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J203A/B & 1401-J202A/B-SPACE HEATER | AMMONIA PLANT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 38 | 247 | 38 | 8 | 34 | 365 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 2.4008 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 365
163 | 1401-P203F | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J203A/B & 1401-J202A/B | AMMONIA PLANT | B | MOTOR | 30 | kW | 3Ph | 400 | 0.85 | 0.954 | 53.4006 | 320.4036 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 30 | 247 | 38 | 8 | 33 | 356 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 2.1467 | YES | 4.6201 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 712
164 | - | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J203A/B & 1401-J202A/B-SPACE HEATER | AMMONIA PLANT | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 30 | 247 | 38 | 8 | 33 | 356 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 2.3416 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 356
165 | 1401-BM203A | EPMCC-1 | BARRING DEVICE MOTOTR FOR 1401-J203A | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.79 | 0.886 | 11.3421 | 68.0527 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 257 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.339 | YES | 4.2984 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 376
X | - | EPMCC-1 | FRAME OIL HEATER FOR 1401-J203A | AMMONIA PLANT | B | POWER | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 120 | 3.5C X 120 | 3.5C X 120 | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 1R x 0.6/1kV x 3.5C x 120 Sqmm
X | - | EPMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J203A | AMMONIA PLANT | A | POWER | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm
X | - | EPMCC-1 | WATER TANK HEATER FOR 1401-J203A | AMMONIA PLANT | B | POWER | 40 | kW | 3Ph | 400 | 0.85 | 0.95 | 71.5006 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 240 | 3.5C X 240 | 3.5C X 240 | 0.6/1.0 | 401 | 0.16 | 0.0719 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 240 Sqmm | 1R x 0.6/1kV x 3.5C x 240 Sqmm
166 | 1401-P203D | EPMCC-1 | AUX. LUBE OIL PUMP FOR 1401-J203B | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.84 | 0.927 | 10.1952 | 61.1712 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 248 | 38 | 8 | 34 | 366 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1617 | YES | 3.761 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 366
X | LATER | EPMCC-1 | MAIN LUBE OIL PUMP FOR1401-J203B | AMMONIA PLANT | B | MOTOR | 15 | kW | 3Ph | 400 | 0.84 | 0.927 | 27.8051 | 166.8306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70+PE Sqmm
X | LATER | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J203B | AMMONIA PLANT | A | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm
X | LATER | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J203B | AMMONIA PLANT | B | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 240 | 3C X 240 | 3C X 240+PE | 0.6/1.0 | 401 | 0.16 | 0.0719 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 240 Sqmm | 1R x 0.6/1kV x 3C x 240+PE Sqmm
167 | 1401-BM203B | EPMCC-1 | BARRING DEVICE MOTOTR FOR 1401-J203B | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.79 | 0.886 | 11.3421 | 68.0527 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 263 | 38 | 8 | 35 | 382 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.3763 | YES | 4.367 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 382
X | - | EPMCC-1 | FRAME OIL HEATER FOR 1401-J203 | AMMONIA PLANT | B | POWER | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 120 | 3.5C X 120 | 3.5C X 120 | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 1R x 0.6/1kV x 3.5C x 120 Sqmm
X | - | EPMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J203 B | AMMONIA PLANT | A | POWER | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm
X | - | EPMCC-1 | WATER TANK HEATER FOR 1401-J203B | AMMONIA PLANT | B | POWER | 40 | kW | 3Ph | 400 | 0.85 | 0.95 | 71.5006 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 240 | 3.5C X 240 | 3.5C X 240 | 0.6/1.0 | 401 | 0.16 | 0.0719 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 240 Sqmm | 1R x 0.6/1kV x 3.5C x 240 Sqmm
168 | 1401-P203A | EPMCC-1 | HPU system motor | AMMONIA PLANT | A | POWER | 11 | kW | 3Ph | 400 | 0.85 | 0.95 | 19.6627 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 263 | 38 | 8 | 35 | 382 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.4026 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 382
169 | - | EPMCC-1 | UCP CABINET (NON-UPS) FOR 1401-J203A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.45 | kW | 1Ph | 230 | 0.85 | 0.95 | 7.8072 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.8047 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145
170 | - | EPMCC-1 | UCP CABINET (REDUNDANT UPS) FOR 1401-J203A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2403 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145
171 | - | EPMCC-1 | ISC PANEL (NON-UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.18 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.96917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.53601 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145
172 | - | EPMCC-1 | ISC PANEL (REDUNDANT UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.81 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3613 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.412 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145
173 | - | EPMCC-1 | HPU system motor | AMMONIA PLANT | A | POWER | 11 | kW | 3Ph | 400 | 0.85 | 0.95 | 19.6627 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 263 | 38 | 8 | 35 | 382 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.4026 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 382
174 | - | EPMCC-1 | UCP CABINET (NON-UPS) FOR 1401-J203B (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.45 | kW | 1Ph | 230 | 0.85 | 0.95 | 7.8072 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.8047 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145
175 | - | EPMCC-1 | UCP CABINET (REDUNDANT UPS) FOR 1401-J203A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2403 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145
176 | - | EPMCC-1 | ISC PANEL (NON-UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.18 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.96917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.53601 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145
177 | - | EPMCC-1 | ISC PANEL (REDUNDANT UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.81 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3613 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.412 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145
Sea water intake outfall package _ Intake facilities/Intake Structure package (connected load)
X | - | EPMCC-1 | MOV ON Screen Backwash pump | SEA WATER INTAKE FACILITY | A | MOTOR | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 10.7251 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 1242 | 38 | 8 | 133 | 1459 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3906 | YES | 3.8476 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm
Cooling Tower package
178 | - | EPMCC-1 | MOV ON COOLING WATER BYPASS LINE | COOLING TOWER AREA | B | MOTOR | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 10.7251 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 190 | 38 | 8 | 28 | 302 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.1839 | YES | 1.7851 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 302
179 | 1421-UPS-5-0001 | EPMCC-1 | OUTGOING FEEDER FOR UPS -1 / MAIN SUBSTATION - FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 212.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 379.8468 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 38 | 20 | 6 | 8 | 8 | 80 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 3 | YES | 1.1534 | YES | NA | NA | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 240
180 | 1421-UPS-5-0001 | EPMCC-1 | OUTGOING FEEDER FOR UPS -1 / MAIN SUBSTATION - FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 212.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 379.8468 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 30 | 20 | 6 | 8 | 7 | 71 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 3 | YES | 1.0236 | YES | NA | NA | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 213
181 | 1421-UPS-5-0001 | EPMCC-1 | OUTGOING FEEDER FOR UPS -1 / MAIN SUBSTATION - FEEDER-3 | MAIN SUBSTATION BUILDING | B | POWER | 212.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 379.8468 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 30 | 20 | 6 | 8 | 7 | 71 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 3 | YES | 1.0236 | YES | NA | NA | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 213
182 | 1421-BC-6-0001 | EPMCC-1 | OUTGOING FEEDER FOR BATTERY CHARGER - MAIN SUBSTATION - FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 100 | kW | 3Ph | 400 | 0.85 | 0.95 | 178.7515 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 0.58008 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 114
183 | 1421-BC-6-0002 | EPMCC-1 | OUTGOING FEEDER FOR BATTERY CHARGER - MAIN SUBSTATION - FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 100 | kW | 3Ph | 400 | 0.85 | 0.95 | 178.7515 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 30 | 0 | 5 | 8 | 5 | 48 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 0.48849 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 96
184 | 1421-EMLDB-4-0001 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-1 (MAIN SUBSTATION BUILDING) | MAIN SUBSTATION BUILDING | A | POWER | 21.25 | kW | 3Ph | 400 | 0.85 | 0.95 | 37.9847 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.2675 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 57
185 | 1420-EMLDB-4-0002 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-2 (COOLING TOWER SUBSTATION) | COOLING TOWER SUBSTATION | B | POWER | 29.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 53.1786 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 30 | 88 | 10 | 8 | 14 | 150 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 1.8015 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 150
186 | 1402-EMLDB-4-0003 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-3 (NH3 STORAGE SUBSTATION) | AMMONIA STORAGE SUBSTATION | B | POWER | 12.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 22.7908 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 365 | 38 | 8 | 45 | 486 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 1.8569 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 486
187 | 1409-EMLDB-4-0004 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-4 (SEA WATER TREATMENT SUBSTATION) | SEA WATER TREATMENT SUBSTATION | A | POWER | 12.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 22.7908 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 38 | 340 | 38 | 8 | 43 | 467 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 2.4037 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 467
188 | 1409-EMLDB-4-0005 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-5 (ELECTROLYZER SUBSTATION) | ELECTROLYZER SUBSTATION | A | POWER | 20 | kW | 3Ph | 400 | 0.85 | 0.95 | 35.7503 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 35 | 144 | 20 | 8 | 21 | 228 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 1.8409 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 228
189 | 1421-ESWG-4-0001 | PMCC-1 | EPMCC-1 (INCOMER-1) | MAIN SUBSTATION BUILDING |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833
190 | 1421-ESWG-4-0001 | PMCC-1 | EPMCC-1 (INCOMER-2) | MAIN SUBSTATION BUILDING |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833
191 | 1421-ESWG-4-0001 | EDG | EPMCC-1 (INCOMER-3 - DG) | MAIN SUBSTATION BUILDING |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833
PDB-1
HVAC SYSTEM
192 | - | PDB-1 | ROOFTOP UNIT-1 | CENTRAL CONTROL BUILDING | A | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.954 | 133.5015 | 801.0089 | 0.2 | 50 | 0 | 0 | TRENCH | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 1.5528 | YES | 3.3418 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 206
193 | - | PDB-1 | ROOFTOP UNIT-1-SPACE HEATER | CENTRAL CONTROL BUILDING | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.6775 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 103
194 | - | PDB-1 | HEATER-1 | CENTRAL CONTROL BUILDING | A | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6168 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103
195 | - | PDB-1 | HUMIDIFIER-1 | CENTRAL CONTROL BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9401 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103
196 | - | PDB-1 | ROOFTOP UNIT-2 | CENTRAL CONTROL BUILDING | B | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.954 | 133.5015 | 801.0089 | 0.2 | 50 | 0 | 0 | TRENCH | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 1.5528 | YES | 3.3418 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 206
197 | - | PDB-1 | ROOFTOP UNIT-2-SPACE HEATER | CENTRAL CONTROL BUILDING | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.6775 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 103
198 | - | PDB-1 | HEATER-2 | CENTRAL CONTROL BUILDING | B | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6168 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103
199 | - | PDB-1 | HUMIDIFIER-2 | CENTRAL CONTROL BUILDING | B | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9401 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103
198 | - | PDB-1 | ROOFTOP UNIT-3 | CENTRAL CONTROL BUILDING | A | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.954 | 133.5015 | 801.0089 | 0.2 | 50 | 0 | 0 | TRENCH | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 1.5528 | YES | 3.3418 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 206
199 | - | PDB-1 | ROOFTOP UNIT-3-SPACE HEATER | CENTRAL CONTROL BUILDING | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.6775 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 103
200 | - | PDB-1 | HEATER-3 | CENTRAL CONTROL BUILDING | A | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6168 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103
201 | - | PDB-1 | HUMIDIFIER-3 | CENTRAL CONTROL BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9401 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103
200 | 1422-ACDB-4-0002 | PDB-1 | HVAC DB-001 | CENTRAL CONTROL BUILDING | B | POWER | 72.623 | kW | 3Ph | 400 | 0.85 | 0.95 | 129.8147 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.2416 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 103
201 | - | PDB-1 | ROOFTOP UNIT1 | MAIN SUBSTATION BUILDING | B | MOTOR | 62 | kW | 3Ph | 400 | 0.85 | 0.954 | 110.3612 | 662.1673 | 0.2 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 2 | YES | 1.2179 | YES | 2.3899 | YES | 2R x 0.6/1kV x 3C x 50 Sqmm | 2R x 0.6/1kV x 3C x 50+PE Sqmm
202 | - | PDB-1 | ROOFTOP UNIT1-SPACE HEATER | MAIN SUBSTATION BUILDING | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.45386 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm
203 | - | PDB-1 | HEATER-1 | MAIN SUBSTATION BUILDING | B | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6959 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm
204 | - | PDB-1 | HUMIDIFIER-1 | MAIN SUBSTATION BUILDING | B | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm
205 | - | PDB-1 | ROOFTOP UNIT2 | MAIN SUBSTATION BUILDING | A | MOTOR | 45 | kW | 3Ph | 400 | 0.85 | 0.954 | 80.1009 | 480.6053 | 0.2 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.7679 | YES | 3.4692 | YES | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50+PE Sqmm
206 | - | PDB-1 | ROOFTOP UNIT2-SPACE HEATER | MAIN SUBSTATION BUILDING | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.45386 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm
207 | - | PDB-1 | HEATER-2 | MAIN SUBSTATION BUILDING | A | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6959 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm
208 | - | PDB-1 | HUMIDIFIER-2 | MAIN SUBSTATION BUILDING | A | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm
205 | - | PDB-1 | VFD ROOM - SPLIT AC 1 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
206 | - | PDB-1 | VFD ROOM - SPLIT AC 2 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
207 | - | PDB-1 | VFD ROOM - SPLIT AC 3 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
208 | - | PDB-1 | VFD ROOM - SPLIT AC 4 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
209 | - | PDB-1 | VFD ROOM - SPLIT AC 5 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
206 | - | PDB-1 | VFD ROOM - SPLIT AC 6 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
207 | - | PDB-1 | VFD ROOM - SPLIT AC 7 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
208 | - | PDB-1 | VFD ROOM - SPLIT AC 8 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
209 | - | PDB-1 | VFD ROOM - SPLIT AC 9 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
210 | - | PDB-1 | VFD ROOM - SPLIT AC 10 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
207 | - | PDB-1 | VFD ROOM - SPLIT AC 11 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103
209 | - | PDB-1 | BATTERY ROOM-VENTILATION FAN 1 | MAIN SUBSTATION BUILDING | A | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.98313 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.14878 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 69
210 | - | PDB-1 | BATTERY ROOM-VENTILATION FAN 2 | MAIN SUBSTATION BUILDING | A | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.98313 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.14878 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 69
211 | - | PDB-1 | LV SWITCHGEAR ROOM VENTILATION FAN 1 | MAIN SUBSTATION BUILDING | A | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 69
212 | - | PDB-1 | LV SWITCHGEAR ROOM VENTILATION FAN 2 | MAIN SUBSTATION BUILDING | A | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 69
213 | - | PDB-1 | LV SWITCHGEAR ROOM VENTILATION FAN 3 | MAIN SUBSTATION BUILDING | A | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 69
214 | - | PDB-1 | MV SWITCHGEAR ROOM VENTILATION FAN 1 | MAIN SUBSTATION BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 2 | YES | 1.6326 | YES | NA | NA | 2R x 0.6/1kV x 4C x 6 Sqmm | 2R x 0.6/1kV x 4C x 6 Sqmm | 138
215 | - | PDB-1 | MV SWITCHGEAR ROOM VENTILATION FAN 2 | MAIN SUBSTATION BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 2 | YES | 1.6326 | YES | NA | NA | 2R x 0.6/1kV x 4C x 6 Sqmm | 2R x 0.6/1kV x 4C x 6 Sqmm | 138
216 | - | PDB-1 | MV SWITCHGEAR ROOM VENTILATION FAN 3 | MAIN SUBSTATION BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 2 | YES | 1.6326 | YES | NA | NA | 2R x 0.6/1kV x 4C x 6 Sqmm | 2R x 0.6/1kV x 4C x 6 Sqmm | 138
217 | - | PDB-1 | ELECTRICAL SHIFT INCHARGE RM - SPLIT AC 1 | MAIN SUBSTATION BUILDING | A | POWER | 4 | kW | 1Ph | 230 | 0.85 | 0.95 | 21.5372 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3691 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm
218 | - | PDB-1 | BATTERY ROOM - SPLIT AC 1 | MAIN SUBSTATION BUILDING | A | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.0729 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69
219 | - | PDB-1 | BATTERY ROOM - SPLIT AC 2 | MAIN SUBSTATION BUILDING | A | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.0729 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69
220 | - | PDB-1 | BATTERY ROOM - SPLIT AC 3 | MAIN SUBSTATION BUILDING | A | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.0729 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69
221 | - | PDB-1 | BATTERY ROOM - SPLIT AC 4 | MAIN SUBSTATION BUILDING | A | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.0729 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69
HVAC - EMERGENCY LOADS
CONTROL BUILDING
222 | - | PDB-1 | GROUND FLOOR - EXHAUST FAN | CENTRAL CONTROL BUILDING | A | POWER | 18 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9762 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 103
223 | - | PDB-1 | GROUND FLOOR - FRESH AIR FAN | CENTRAL CONTROL BUILDING | A | POWER | 18 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9762 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 103
224 | - | PDB-1 | UPS ROOM - EXHAUST FAN | CENTRAL CONTROL BUILDING | A | POWER | 1.1 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9762 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 103
225 | - | PDB-1 | BATTERY ROOM - EXHAUST FAN | CENTRAL CONTROL BUILDING | A | POWER | 1.1 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9762 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 103
Other Load
222 | 1421-ACDB-4-0001 | PDB-1 | OUTGOING FEEDER FOR 400V ACDB-1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 31.0737 | kW | 3Ph | 400 | 0.85 | 0.95 | 55.5447 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.008 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 31
223 | 1421-ACDB-4-0001 | PDB-1 | OUTGOING FEEDER FOR 400V ACDB-1 / FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 31.0737 | kW | 3Ph | 400 | 0.85 | 0.95 | 55.5447 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.008 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 31
224 | 1421-PDB-4-0001 | PMCC-1 | PDB - 1 (INCOMER 1) | MAIN SUBSTATION BUILDING |  | INCOMER | 343.1937 | kW | 3Ph | 400 | 0.85 | 0.951 | 612.8186
225 | 1421-PDB-4-0001 | PMCC-1 | PDB - 1 (INCOMER 2) | MAIN SUBSTATION BUILDING |  | INCOMER | 343.1937 | kW | 3Ph | 400 | 0.85 | 0.951 | 612.8186
ACDB-1
226 | 1421-SWG-1-0001 | ACDB-1 | AUX POWER SUPPLY - 33kV SWITCHGEAR - 1 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 36 | 0 | 5 | 8 | 5 | 54 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.0574 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 54
227 | 1421-SWG-1-0001 | ACDB-1 | AUX POWER SUPPLY - 33kV SWITCHGEAR - 2 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 36 | 0 | 5 | 8 | 5 | 54 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.0574 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 54
228 | 1421-SWG-2-0001 | ACDB-1 | AUX POWER SUPPLY - 11kV SWITCHGEAR - 1 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 25 | 0 | 5 | 8 | 4 | 42 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.8224 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 42
229 | 1421-SWG-2-0001 | ACDB-1 | AUX POWER SUPPLY - 11kV SWITCHGEAR - 2 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 0 | 5 | 8 | 5 | 48 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.93988 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 48
230 | 1421-SWG-4-0001 | ACDB-1 | AUX POWER SUPPLY - PMCC-1 (BUS-A) | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.60701 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 31
231 | 1421-SWG-4-0001 | ACDB-1 | AUX POWER SUPPLY - PMCC-1 (BUS-B) | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.60701 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 31
232 | 1421-TFP-1-0001 | ACDB-1 | AUX POWER SUPPLY - POWER TRANSFORMER - 1 | MAIN SUBSTATION BUILDING |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 5 | 8 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.9581 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 50
233 | 1421-TFP-1-0002 | ACDB-1 | AUX POWER SUPPLY - POWER TRANSFORMER - 2 | MAIN SUBSTATION BUILDING |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 39 | 0 | 5 | 8 | 6 | 58 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.2714 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 58
234 | 1421-SWG-2-0001 | ACDB-1 | AUX POWER SUPPLY SEGREGATED PHASE BUSDUCT SYSTEM-1A | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 34 | 0 | 5 | 8 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.0182 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52
235 | 1421-SWG-2-0001 | ACDB-1 | AUX POWER SUPPLY SEGREGATED PHASE BUSDUCT SYSTEM-1B | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 41 | 0 | 5 | 8 | 6 | 60 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.1749 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 60
236 | 1421-SWG-4-0001 | ACDB-1 | AUX POWER SUPPLY NSPBD SYSTEM-1A | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 9 | 0 | 5 | 8 | 3 | 25 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.48952 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 25
237 | 1421-SWG-4-0001 | ACDB-1 | AUX POWER SUPPLY NSPBD SYSTEM-1B | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.60701 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 31
238 | 1421-TFD-2-0001 | ACDB-1 | AUX POWER SUPPLY DISTRIBUTION TRANSFORMER-1 | MAIN SUBSTATION BUILDING |  | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.3569 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 28 | 0 | 5 | 8 | 5 | 46 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.54043 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 46
239 | 1421-TFD-2-0002 | ACDB-1 | AUX POWER SUPPLY DISTRIBUTION TRANSFORMER-2 | MAIN SUBSTATION BUILDING |  | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.3569 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 21 | 0 | 5 | 8 | 4 | 38 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.44644 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 38
240 | 1421-TFP-1-0001 | ACDB-1 | POWER TRANSFORMER OLTC-1 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 43 | 0 | 5 | 8 | 6 | 62 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.214 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 62
241 | 1421-TFP-1-0002 | ACDB-1 | POWER TRANSFORMER OLTC-2 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 43 | 0 | 5 | 8 | 6 | 62 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.214 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 62
242 | 1421-ACDB-4-0001 | PDB-1 | ACDB-1 (INCOMER 1) | MAIN SUBSTATION BUILDING |  | INCOMER | 28.2316 | kW | 3Ph | 400 | 0.85 | 0.951 | 50.4113
243 | 1421-ACDB-4-0001 | PDB-1 | ACDB-1 (INCOMER 2) | MAIN SUBSTATION BUILDING |  | INCOMER | 28.2316 | kW | 3Ph | 400 | 0.85 | 0.951 | 50.4113
MLDB-1
244 | NLP-001 | MLDB-01 | LIGHTING DB-001 | MAIN SUBSTATION BUILDING |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 27 | 0 | 5 | 5 | 4 | 41 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.31236 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 41
245 | NLP-002 | MLDB-01 | LIGHTING DB-002 | CENTRAL CONTROL BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 27 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.26284 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 69
246 | NLP-003 | MLDB-01 | LIGHTING DB-003 | ASU PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 25 | 95 | 22 | 10 | 16 | 168 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.63996 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 168
247 | NLP-004 | MLDB-01 | LIGHTING DB-004 | AMMONIA PLANT |  | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.951 | 26.7845 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 25 | 205 | 38 | 10 | 28 | 306 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 1.851 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 306
248 | NLP-005 | MLDB-01 | LIGHTING DB-005 | INSTRUMENT AIR PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 25 | 176 | 15 | 5 | 23 | 244 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.92947 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 244
249 | NLP-006 | MLDB-01 | LIGHTING DB-006 | HYDROGEN STORAGE AREA |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 25 | 370 | 43 | 5 | 45 | 488 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 1.968 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 488
250 | NLP-007 | MLDB-01 | STREET LIGHTING DB- 01 | MAIN SUBSTATION BUILDING |  | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.951 | 26.7845 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 0 | 10 | 5 | 5 | 49 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.55996 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 49
251 | HM-001 | MLDB-01 | HIGH MAST-001 | NEAR HYDROGEN STORAGE AREA |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 405 | 10 | 5 | 47 | 515 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.2555 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 515
252 | HM-002 | MLDB-01 | HIGH MAST-002 | NEAR HYDROGEN STORAGE AREA |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 525 | 10 | 5 | 59 | 647 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.5773 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 647
253 | HM-003 | MLDB-01 | HIGH MAST-003 | NEAR HYDROGEN STORAGE AREA |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 405 | 10 | 5 | 47 | 515 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.2555 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 515
254 | HM-004 | MLDB-01 | HIGH MAST-004 | NEAR HYDROGEN STORAGE AREA |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 525 | 10 | 5 | 59 | 647 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.5773 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 647
255 | HM-005 | MLDB-01 | HIGH MAST-005 | NEAR MAIN SUBSTATION AREA FIRE DRILL POINT |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 50 | 10 | 5 | 12 | 125 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.30474 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 125
256 | 1421-MLDB-4-0001 | PMCC-1 | MAIN LIGHTING DB-001 (INCOMER-1) | MAIN SUBSTATION BUILDING |  | INCOMER | 127.5 | kW | 3Ph | 400 | 0.85 | 0.951 | 320
257 | 1421-MLDB-4-0001 | PMCC-1 | MAIN LIGHTING DB-001 (INCOMER-2) | MAIN SUBSTATION BUILDING |  | INCOMER | 127.5 | kW | 3Ph | 400 | 0.85 | 0.951 | 320
EMLDB-1
258 | ELP-001 | EMLDB-1 | EMERGENCY LIGHTING DB-001 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 12 | 0 | 5 | 5 | 3 | 25 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 0.32802 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 25
259 | ELP-002 | EMLDB-1 | EMERGENCY LIGHTING DB-002 | CENTRAL CONTROL BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | TRENCH | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 30 | 26 | 10 | 5 | 8 | 79 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 1.0365 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 79
260 | ELP-003 | EMLDB-01 | EMERGENCY LIGHTING DB-003 | ASU PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 36 | 96 | 22 | 10 | 17 | 181 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 2.3749 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 181
261 | ELP-004 | EMLDB-01 | EMERGENCY LIGHTING DB-004 | AMMONIA PLANT |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 36 | 206 | 38 | 10 | 29 | 319 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.4303 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 319
262 | ELP-005 | EMLDB-01 | EMERGENCY LIGHTING DB-005 | INSTRUMENT AIR PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 36 | 177 | 15 | 5 | 24 | 257 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.1033 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 257
263 | ELP-006 | EMLDB-01 | EMERGENCY LIGHTING DB-006 | HYDROGEN STORAGE AREA |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 |  | 371 | 43 | 5 | 42 | 461 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4096 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 461
264 | ELP-007 | EMLDB-01 | EMERGENCY STREET LIGHTING DB- 01 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 29 | 0 | 10 | 5 | 5 | 49 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 0.64292 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 49
265 | 1421-EMLDB-4-0001 | EMLDB-1 | EMERGENCY MAIN LIGHTING DB-001 (INCOMER) | MAIN SUBSTATION BUILDING |  | INCOMER | 30 | kW | 3Ph | 400 | 0.85 | 0.951 | 63
WDB-1
266 | WSDB-001 | WDB-01 | POWER RECEPTACLE DB-001 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 13 | 0 | 5 | 5 | 3 | 26 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.099041 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 26
267 | WSDB-002 | WDB-01 | POWER RECEPTACLE DB-002 | CENTRAL CONTROL BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 28 | 25 | 10 | 5 | 7 | 75 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.2857 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 75
268 | WSDB-003 | WDB-01 | POWER RECEPTACLE DB-003 | ASU PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 35 | 97 | 22 | 10 | 17 | 181 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.68948 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 181
269 | WSDB-004 | WDB-01 | POWER RECEPTACLE DB-004 | AMMONIA PLANT |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 35 | 207 | 38 | 10 | 29 | 319 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.2152 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 319
270 | WSDB-005 | WDB-01 | POWER RECEPTACLE DB-005 | INSTRUMENT AIR PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 35 | 178 | 15 | 5 | 24 | 257 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.97899 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 257
271 | WSDB-006 | WDB-01 | POWER RECEPTACLE DB-006 | HYDROGEN STORAGE AREA |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 371 | 43 | 5 | 44 | 483 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.8399 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 483
272 | WS-001 & 002 | WDB-01 | WELDING SOCKET -001 & 002 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 15 | 0 | 5 | 5 | 3 | 28 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.22915 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 28
273 | WS-003 | WDB-01 | WELDING SOCKET -003 | CENTRAL CONTROL BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 28 | 30 | 10 | 5 | 8 | 81 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.66291 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 81
274 | WS-004 & 005 | WDB-01 | WELDING SOCKET -004 & 005 | ASU/ INSTRUMENT AIR PACKAGE |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 36 | 97 | 22 | 8 | 17 | 180 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.4731 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 180
275 | WS-006 & 007 | WDB-01 | WELDING SOCKET -006 & 007 | AMMONIA PLANT |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 36 | 207 | 38 | 8 | 29 | 318 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6621 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 318
276 | 1421-WDB-4-0001 | PMCC-1 | WELDING & RECEPTACLE DB-001 (INCOMER) | MAIN SUBSTATION BUILDING |  | INCOMER | 42.5 | kW | 3Ph | 400 | 0.85 | 0.951 | 320
MAIN UPS DB-1
277 | 1422-UPS-SDB-4-0001 | MAIN UPS DB-1 | AC UPS SUB DB-1_FEEDER-1 | CENTRAL CONTROL BUILDING |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 320 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 12 | 14 | 5 | 8 | 4 | 43 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 0.78339 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 86
278 | 1422-UPS-SDB-4-0001 | MAIN UPS DB-1 | AC UPS SUB DB-1_FEEDER-2 | CENTRAL CONTROL BUILDING |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 320 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 12 | 14 | 5 | 8 | 4 | 43 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 0.78339 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 86
279 | 1417-UPS-SDB-4-0002 | MAIN UPS DB-1 | AC UPS SUB DB-2_FEEDER | Electrolyzer Electrical Building |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 20 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 55 | 101 | 20 | 8 | 19 | 203 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.3768 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 203
280 | 1417-UPS-SDB-4-0003 | MAIN UPS DB-1 | AC UPS SUB DB-3_FEEDER | Electrolyzer Electrical Building |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 20 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 55 | 101 | 20 | 8 | 19 | 203 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.3768 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 203
281 | 1402-UPS-SDB-4-0004 | MAIN UPS DB-1 | AC UPS SUB DB-4_FEEDER-1 | Ammonia Storage Substation |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 16 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 7 | 373 | 20 | 8 | 41 | 449 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.298 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 449
282 | 1402-UPS-SDB-4-0004 | MAIN UPS DB-1 | AC UPS SUB DB-4_FEEDER-2 | Ammonia Storage Substation |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 16 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 7 | 373 | 20 | 8 | 41 | 449 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.298 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 449
283 | 1409-UPS-SDB-4-0005 | MAIN UPS DB-1 | AC UPS SUB DB-5_FEEDER-1 | Sea Water Treatment Substation |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 32 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 332 | 20 | 8 | 39 | 429 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.3015 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 429
284 | 1409-UPS-SDB-4-0005 | MAIN UPS DB-1 | AC UPS SUB DB-5_FEEDER-2 | Sea Water Treatment Substation |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 32 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 332 | 20 | 8 | 39 | 429 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.3015 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 429
285 | 1422-UPSDB-4-0001 | UPS-1 | AC UPSDB-1 (INCOMER-1) | CENTRAL CONTROL BUILDING |  | INCOMER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 400
286 | 1422-UPSDB-4-0001 | UPS-1 | AC UPSDB-1 (INCOMER-2) | CENTRAL CONTROL BUILDING |  | INCOMER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 400
CENTRAL CONTROL BUILDING HVAC DB
287 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - VENTILATION FAN 1 | CENTRAL CONTROL BUILDING |  | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.951 | 0.9821 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.12708 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 59
288 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM 2 - VENTILATION FAN 2 | CENTRAL CONTROL BUILDING |  | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.951 | 0.9821 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.12708 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 59
289 |  | CENTRAL CONTROL BUILDING HVAC DB | LADIES & GENTS TOILET - VENTILATION FAN | CENTRAL CONTROL BUILDING |  | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.951 | 0.9821 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.12708 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 59
290 |  | CENTRAL CONTROL BUILDING HVAC DB | CLEAN AGENT ROOM | CENTRAL CONTROL BUILDING |  | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.951 | 0.9821 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.12708 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 59
291 |  | CENTRAL CONTROL BUILDING HVAC DB | UPS ROOM - SPLIT AC 1 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
292 |  | CENTRAL CONTROL BUILDING HVAC DB | UPS ROOM - SPLIT AC 2 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
293 |  | CENTRAL CONTROL BUILDING HVAC DB | UPS ROOM - SPLIT AC 3 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
294 |  | CENTRAL CONTROL BUILDING HVAC DB | UPS ROOM - SPLIT AC 4 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
295 |  | CENTRAL CONTROL BUILDING HVAC DB | INSTRUMENTATION MANAGER - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
296 |  | CENTRAL CONTROL BUILDING HVAC DB | APC/MES MANAGER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
297 |  | CENTRAL CONTROL BUILDING HVAC DB | GENTS PRAYER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 8.068 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8156 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 59
298 |  | CENTRAL CONTROL BUILDING HVAC DB | LADIES PRAYER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
299 |  | CENTRAL CONTROL BUILDING HVAC DB | SHIFT INCHARGE ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 8.068 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8156 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 59
300 |  | CENTRAL CONTROL BUILDING HVAC DB | NH3 PLANT MANAGER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
301 |  | CENTRAL CONTROL BUILDING HVAC DB | PRODUCTION SR MANAGER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
302 |  | CENTRAL CONTROL BUILDING HVAC DB | CONFERENCE ROOM - SPLIT AC 1 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
303 |  | CENTRAL CONTROL BUILDING HVAC DB | CONFERENCE ROOM - SPLIT AC 2 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
304 |  | CENTRAL CONTROL BUILDING HVAC DB | CONFERENCE ROOM - SPLIT AC 2 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
305 |  | CENTRAL CONTROL BUILDING HVAC DB | DINING ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
X |  | CENTRAL CONTROL BUILDING HVAC DB | SHIFT IN-CHARGE ROOM-SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.951 | 0 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 0 | YES | #DIV/0! | #DIV/0! | NA | NA | 0R x 0.6/1kV x 3C x 4 Sqmm | 0R x 0.6/1kV x 3C x 4 Sqmm
306 |  | CENTRAL CONTROL BUILDING HVAC DB | WAITING HALL - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 8.068 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8156 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 59
307 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - SPLIT AC 1 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
308 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - SPLIT AC 2 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
309 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - SPLIT AC 3 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
310 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - SPLIT AC 4 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57
311 | 1422-ACDB-4-0002 | PDB-1 | HVAC DB-2 INCOMER | CENTRAL CONTROL BUILDING |  | INCOMER | 31.0737 | kW | 3Ph | 400 | 0.85 | 0.951 | 55.4863
[33 empty] | 74524.5 | [15 empty] | #N/A

## MV Cable sizing-6.6kV (hidden)
MV (6.6kV) CABLE SIZING
Sl. No | LOAD | [13 empty] | SHORT CIRCUIT CURRENT WITHSTAND CAPABILITY |  |  | CABLE DATA | [12 empty] | DERATING FACTOR | [5 empty] | CURRENT CARRYING CAPACITY |  |  | RUNNING CONDITION VOLTAGE DROP |  |  |  | MOTOR STARTING VOLTAGE DROP |  | Selected Cable Size
| Description | Unit | Equipment Location | Location As per Plot Plan | Type of feeder | Rated power | UNIT (kW / kVA) | 3Phase / 1Phase | Rated Voltage (V) | Power factor | Efficiency | Rated full load current | Motor starting current | Motor starting power factor | Short circuit current of switchboard (kA) | Short circuit current withstand duration (sec) | Minimum size required for Short circuit withstand capacity (Sq.mm) | Installation | No. of Cores | Size in (Sq.mm) | Cable size | Cable size With (PE) Core | Cable Voltage (kV) | Current Rating of the Cable (A) | Cable resistance at 90°C (Ohm / Ph / km) | Cable reactance at 50Hz (Ohm / Ph / km) | Cable Length with in Electrical Building (m) | Cable Length from Electrical Building to Equipment (m) | Cable length both side dropping & Termination (m) | Cable length (m) | Ambient temperature (K1) | Grouping factor (K2) | Ground temperature (K3) | Depth of laying (K4) | Thermal resistivity of ground (K5) | Overall derating factor | Derated current carrying capacity (A) | No. of Runs | Derated current > Rated current | % VOLTAGE DROP DURING RUNNING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT (YES/NO) | (HIDE) | Maximum length under Allowable voltage drop | % VOLTAGE DROP DURING STARTING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT DURING STARTING CONDITION (YES/NO) | Selected cable size | Total Length in meters | No. of End Termination | Remarks | Dia of the conductor(mm) | Total Dia of the conductor(mm)
[37 empty] | A | [5 empty] | Meters
6.6kV MV Switchgear
1 | Incomer-1 from Unit Auxiliary Transformer (11/6.9kV)-1 | COMMON |  |  | I | 12500 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 1151.051 | 0 | 0.00 | 40 | 1 | 279.7203 | AIR | 3C | 185 | 3C X 185 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 166 | 15 | 226 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 63 | #REF! | #REF!
1a | Unit Auxiliary Transformer (11/6.9kV)-1 NGR | COMMON |  |  | I |  | kVA | 1Phase | 6600 | 0.85 | 0.95 | 400 | 0 | 0.00 | 0.3 | 10 | 6.6341 | AIR | 1C | 185 | 1C X 185 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 5 | 20 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 63 | #REF!
2 | Incomer-2 from Unit Auxiliary Transformer (11/6.9kV)-2 | COMMON |  |  | I | 12500 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 1151.051 | 0 | 0.00 | 40 | 1 | 279.7203 | AIR | 3C | 185 | 3C X 185 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 206 | 15 | 266 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 63 | #REF!
2a | Unit Auxiliary Transformer (11/6.9kV)-2 NGR | COMMON |  |  | I |  | kVA | 1Phase | 6600 | 0.85 | 0.95 | 400 | 0 | 0.00 | 0.3 | 10 | 6.6341 | AIR | 1C | 185 | 1C X 185 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 5 | 20 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 63 | #REF!
3 | Incomer from BSDG 6.6kV Switchgear incomer-1 | COMMON |  |  | I | 2000 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 184.1682 | 0 | 0.00 | 40 | 1 | 279.7203 | AIR | 3C | 150 | 3C X 150 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 185 | 15 | 245 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | 2 | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | 2R x 0.6/1kV x 3C x 150 Sqmm | 490 | 4 |  | 58 | 116
4 | Incomer from BSDG 6.6kV Switchgear incomer-2 | COMMON |  |  | I | 2000 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 184.1682 | 0 | 0.00 | 40 | 1 | 279.7203 | AIR | 3C | 150 | 3C X 150 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 185 | 15 | 245 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | 2 | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | 2R x 0.6/1kV x 3C x 150 Sqmm | 490 | 4 |  | 58 | 116
5 | Incomer from BSDG 6.6kV Switchgear incomer-3 | COMMON |  |  | I | 2000 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 184.1682 | 0 | 0.00 | 40 | 1 | 111.8881 | AIR | 3C | 150 | 3C X 185 |  | 3.8/6.6 | 453 | 0.128 | 0.084 | 45 | 185 | 15 | 245 | 0.91 | 0.97 | NA | NA | NA | 0.8827 | 399.8631 | 2 | YES | 0.090615 | YES | 28.1869 | 23415139.8433 | NA | NA | 2R x 0.6/1kV x 3C x 150 Sqmm | 490 | 4 |  | 58 | 116
6 | Incomer from BSDG 6.6kV Switchgear incomer-4 | COMMON |  |  | I | 2000 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 184.1682 | 0 | 0.00 | 40 | 1 | 111.8881 | AIR | 3C | 150 | 3C X 185 |  | 3.8/6.6 | 453 | 0.128 | 0.084 | 45 | 185 | 15 | 245 | 0.91 | 0.97 | NA | NA | NA | 0.8827 | 399.8631 | 2 | YES | 0.090615 | YES | 28.1869 | 23415139.8433 | NA | NA | 2R x 0.6/1kV x 3C x 150 Sqmm | 490 | 4 |  | 58 | 116
7 | CPP-Distribution Transformer-1 (6.6/0.72kV) (GTG PMCC-690V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 56 | #REF!
8 | CPP-Distribution Transformer-2 (6.6/0.72kV) (GTG PMCC-690V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 56 | #REF!
9 | CPP-Distribution Transformer-3 (6.6/0.42kV) (STG PMCC-400V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 56 | #REF!
10 | CPP-Distribution Transformer-4 (6.6/0.422kV) (STG PMCC-400V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 56 | #REF!
11 | CPP-Distribution Transformer-1 (6.6/0.72kV) (GTG PMCC-690V) | COMMON |  |  | P | 720 | kVA | 3Phase | 6600 | 0.86 | 1 | 55.11 | 0 | 0.00 | 0 | 0.16 | 0 | AIR | 3C | 185 | 3C X 185 |  | 3.8/6.6 | #REF! | 0.723 | 0.084 | 15 | 0 | 10 | 225 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | 76.56 | 1 | YES | 0.21628 | YES | 36.6286 | 9009360.886 | NA | NA | 1R x 0.6/1kV x 3C x 185 Sqmm | 225 | 2 |  | 56 | 56
12 | CPP-Distribution Transformer-2 (6.6/0.72kV) (GTG PMCC-690V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 56 | #REF!
13 | CPP-Distribution Transformer-3 (6.6/0.42kV) (STG PMCC-400V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 56 | #REF!
14 | CPP-Distribution Transformer-4 (6.6/0.42kV) (STG PMCC-400V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 56 | #REF!
17 | CAPACITOR BANK FEEDER-1 | COMMON |  |  | P |  | kVA | 3Phase | 6600 | 0.85 | 0.95 | 0 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
18 | CAPACITOR BANK FEEDER-2 | COMMON |  |  | P |  | kVA | 3Phase | 6600 | 0.85 | 0.95 | 0 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
11 | GT FUEL COMPRESSOR MOTOR-1 | COMMON | Fuel Gas receiving & metering station | 25 | M | 1601.5 | kW | 3Phase | 6600 | 0.85 | 0.95 | 173.4972 | 1040.9835 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 271 | 15 | 331 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 56 | #REF! | #REF!
12 | GT FUEL COMPRESSOR MOTOR-2 | COMMON | Fuel Gas receiving & metering station | 25 | M | 1601.5 | kW | 3Phase | 6600 | 0.85 | 0.95 | 173.4972 | 1040.9835 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 311 | 15 | 371 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 56 | #REF!
13 | GT FUEL COMPRESSOR MOTOR-3 (STANDBY) | COMMON | Fuel Gas receiving & metering station | 25 | M | 1601.5 | kW | 3Phase | 6600 | 0.85 | 0.95 | 173.4972 | 1040.9835 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 311 | 15 | 371 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 56 | #REF!
14 | HRSG FEED WATER PUMP-1 | COMMON | STG Building | 31 | M | 713.6 | kW | 3Phase | 6600 | 0.85 | 0.95 | 77.3073 | 463.8438 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 271 | 15 | 331 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 56 | #REF!
15 | HRSG FEED WATER PUMP-2 | COMMON | STG Building | 31 | M | 713.6 | kW | 3Phase | 6600 | 0.85 | 0.95 | 77.3073 | 463.8438 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 271 | 15 | 331 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 56 | #REF!
16 | HRSG WATER PUMP-3 (STANDBY) | COMMON | STG Building | 31 | M | 713.6 | kW | 3Phase | 6600 | 0.85 | 0.95 | 77.3073 | 463.8438 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 45 | 271 | 15 | 331 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 56 | #REF!
19 | Load commutating invertor (SFC) | COMMON |  |  | P | 2388.092 | kW | 3Phase | 6600 | 0.85 | 1 | 245.7765 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | #REF! | #REF! | #REF! | 15 | 0 | 10 | 25 | #REF! | #REF! | #REF! | #REF! | NA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | NA | NA | #REF! | #REF! | #REF! |  | 56 | #REF!
#REF!

## Catalogue A_old (hidden)
LV Cable Catalogue (KEC/RPG Make Catalogue Attached) | [7 empty] | DERATING FACTORS
1-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | LV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) 4 trafoil groups, 6 tier trays with Touching |  | Ground temperature (35°C) (K3) | Depth of laying (900 mm) (K4) |  | Thermal resistivity of ground (1.2 K.m/W) (K5)
| Air | Ground | Duct | [6 empty] | Single core (Trefoil Formation with Touching) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 185 | 370 | 290 | 224 | 0.21 | 0.0875 | 26 | 400 | AIR | 1 | 0.9 | 0.66 | NA | NA | NA
1C X 240 | 445 | 340 | 283 | 0.16 | 0.0866 | 28 |  | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98 | 1.5 | 1.09 | 1.05
1C X 300 | 514 | 382 | 317 | 0.128 | 0.0857 | 31 |  | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98 | 2.5 | 1.09 | 1.05
1C X 400 | 605 | 437 | 370 | 0.1 | 0.0855 | 34 |  | Trench with cover | 1 | 0.81 | 0.78 | NA | NA | NA | 4 | 1.09 | 1.05
1C X 500 | 704 | 500 | 428 | 0.0774 | 0.0851 | 38 | [8 empty] | 6 | 1.09 | 1.05
1C X 630 | 822 | 565 | 464 | 0.06 | 0.0843 | 42 | [8 empty] | 10 | 1.09 | 1.06
[15 empty] | 16 | 1.09 | 1.06
2-core cable |  |  |  |  | 0.6/1.0 kV (E) | [9 empty] | 25 | 1.09 | 1.08
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | [8 empty] | 35 | 1.09 | 1.08
| Air | Ground | Duct | [11 empty] | 50 | 1.09 | 1.08
2C X 1.5 | 29 | 33 | 29 | 15.5 | 0.108 | 12 | [8 empty] | 70 | 1.1 | 1.08
2C X 2.5 | 39 | 43 | 37 | 9.48 | 0.1007 | 13 | [8 empty] | 95 | 1.1 | 1.08
2C X 4 | 48 | 54 | 46 | 5.9 | 0.0947 | 14 | [8 empty] | 120 | 1.1 | 1.08
2C X 6 | 59 | 66 | 58 | 3.94 | 0.0902 | 15 | [8 empty] | 150 | 1.1 | 1.09
2C X 10 | 62 | 70 | 57 | 3.94 | 0.0852 | 17 | [8 empty] | 185 | 1.1 | 1.09
2C X 16 | 79 | 90 | 75 | 2.44 | 0.0815 | 18 | [8 empty] | 240 | 1.1 | 1.09
2C X 25 | 108 | 117 | 99 | 1.54 | 0.0816 | 20 | [8 empty] | 300 | 1.1 | 1.09
2C X 35 | 143 | 140 | 117 | 1.11 | 0.0794 | 21 | [8 empty] | 400 | 1.11 | 1.1
2C X 50 | 173 | 168 | 143 | 0.82 | 0.0792 | 24 | [8 empty] | 500 | 1.11 | 1.1
2C X 70 | 212 | 202 | 177 | 0.567 | 0.0752 | 27 | [8 empty] | 630 | 1.11 | 1.1
2C X 95 | 257 | 243 | 217 | 0.41 | 0.0734 | 30
2C X 120 | 295 | 273 | 247 | 0.324 | 0.0726 | 32
2C X 150 | 342 | 310 | 305 | 0.264 | 0.0732 | 35
2C X 185 | 395 | 350 | 345 | 0.21 | 0.0727 | 39
2C X 240 | 465 | 401 | 393 | 0.16 | 0.0719 | 44
2C X 300 | 532 | 458 | 453 | 0.128 | 0.0711 | 48
2C X 400 | 622 | 505 | 553 | 0.1 | 0.0705 | 54
3-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
3C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
3C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 14
3C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 15
3C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 16
3C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 19
3C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 19
3C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 21
3C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 23
3C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 26
3C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 30
3C X 95 | 221 | 198 | 168 | 0.41 | 0.0734 | 33
3C X 120 | 257 | 225 | 189 | 0.324 | 0.0726 | 35
3C X 150 | 293 | 252 | 210 | 0.264 | 0.0732 | 39
3C X 185 | 338 | 285 | 243 | 0.21 | 0.0727 | 43
3C X 240 | 401 | 330 | 282 | 0.16 | 0.0719 | 48
3C X 300 | 459 | 371 | 316 | 0.128 | 0.0711 | 53
3C X 400 | 536 | 423 | 282 | 0.1 | 0.0705 | 59
4-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
4C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
4C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
4C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
4C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
4C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 20
4C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 21
3.5C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 25
3.5C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 27
3.5C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 30
3.5C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 36
3.5C X 95 | 221 | 198 | 168 | 0.41 | 0.0734 | 39
3.5C X 120 | 257 | 225 | 189 | 0.324 | 0.0726 | 43
3.5C X 150 | 293 | 252 | 210 | 0.264 | 0.0732 | 48
3.5C X 185 | 338 | 285 | 243 | 0.21 | 0.0727 | 53
3.5C X 240 | 401 | 330 | 282 | 0.16 | 0.0719 | 58
3.5C X 300 | 459 | 371 | 316 | 0.128 | 0.0711 | 64
3.5C X 400 | 536 | 423 | 282 | 0.1 | 0.0705 | 72
5-Core Cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
5C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
5C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
5C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
5C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
5C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 20
5C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 20
5C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 24
5C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 26
5C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 29
5C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 33
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 230 | 186 | 176 | 0.568 | 0.125 | 26 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 280 | 221 | 210 | 0.411 | 0.12 | 27 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 324 | 252 | 240 | 0.325 | 0.115 | 29 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 368 | 281 | 267 | 0.265 | 0.114 | 30 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 424 | 317 | 303 | 0.211 | 0.109 | 33 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 502 | 367 | 350 | 0.161 | 0.105 | 35 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 577 | 414 | 397 | 0.13 | 0.102 | 38 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 673 | 470 | 451 | 0.102 | 0.098 | 41 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 757 | 519 | 493 | 0.08 | 0.096 | 46 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 876 | 586 | 557 | 0.063 | 0.094 | 50
1C X 800 | 1005 | 655 | 622 | 0.051 | 0.09 | 54
1C X 1000 | 1138 | 723 | 687 | 0.043 | 0.088 | 58
Three core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 196 | 171 | 150 | 0.568 | 0.097 | 49
3C X 95 | 238 | 24 | 180 | 0.411 | 0.093 | 52
3C X 120 | 274 | 232 | 206 | 0.325 | 0.09 | 56
3C X 150 | 309 | 259 | 231 | 0.265 | 0.088 | 58
3C X 185 | 354 | 293 | 262 | 0.211 | 0.085 | 63
3C X 240 | 415 | 338 | 304 | 0.162 | 0.083 | 69
3C X 300 | 472 | 380 | 343 | 0.13 | 0.082 | 75
3C X 400 | 545 | 432 | 393 | 0.102 | 0.08 | 84
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 6/10 (12)kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 230 | 186 | 176 | 0.568 | 0.125 | 27 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 280 | 221 | 210 | 0.411 | 0.12 | 29 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 324 | 252 | 240 | 0.325 | 0.115 | 30 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 368 | 281 | 267 | 0.265 | 0.114 | 33 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 424 | 317 | 303 | 0.211 | 0.109 | 34 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 502 | 367 | 350 | 0.161 | 0.105 | 36 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 577 | 414 | 397 | 0.13 | 0.102 | 39 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 673 | 470 | 451 | 0.102 | 0.098 | 42 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 757 | 519 | 493 | 0.08 | 0.096 | 46 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 876 | 586 | 557 | 0.063 | 0.094 | 50
1C X 800 | 1005 | 655 | 622 | 0.051 | 0.09 | 54
1C X 1000 | 1138 | 723 | 687 | 0.043 | 0.088 | 59
Three core cable |  |  |  | 6/10 (12)kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 196 | 171 | 150 | 0.568 | 0.103 | 52
3C X 95 | 238 | 204 | 180 | 0.411 | 0.099 | 55
3C X 120 | 274 | 232 | 206 | 0.325 | 0.095 | 59
3C X 150 | 309 | 259 | 231 | 0.265 | 0.093 | 62
3C X 185 | 354 | 293 | 262 | 0.211 | 0.089 | 66
3C X 240 | 415 | 338 | 304 | 0.162 | 0.087 | 72
3C X 300 | 472 | 380 | 343 | 0.13 | 0.084 | 78
3C X 400 | 545 | 432 | 393 | 0.102 | 0.081 | 84
HV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 150mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1500 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.5 K.m/W) (K5) |  |  | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core | Single core | Single core | Multi core | Multi core
1C X 70 | 230 | 186 | 176 | 0.568 | 0.146 | 38 | 33000V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 280 | 221 | 210 | 0.411 | 0.14 | 39 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.95 | 120 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 120 | 324 | 252 | 240 | 0.325 | 0.134 | 41 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.96 | 150 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 150 | 368 | 281 | 267 | 0.265 | 0.132 | 43 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 185 | 424 | 317 | 303 | 0.211 | 0.126 | 45 | [8 empty] | 240 | 1.09 | 1.05 | 1.14 | 0.91 | 1.1 | 0.93
1C X 240 | 502 | 367 | 350 | 0.161 | 0.122 | 47 | [8 empty] | 300 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 300 | 577 | 414 | 397 | 0.13 | 0.118 | 50 | [8 empty] | 400 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 400 | 673 | 470 | 451 | 0.102 | 0.113 | 53 | [8 empty] | 500 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 500 | 757 | 519 | 493 | 0.08 | 0.109 | 56 | [8 empty] | 630 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 630 | 876 | 586 | 557 | 0.063 | 0.105 | 60
1C X 800 | 1005 | 655 | 622 | 0.051 | 0.101 | 65
1C X 1000 | 1138 | 723 | 687 | 0.043 | 0.099 | 69
Three core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 196 | 171 | 150 | 0.568 | 0.129 | 76
3C X 95 | 238 | 204 | 180 | 0.411 | 0.124 | 79
3C X 120 | 274 | 232 | 206 | 0.325 | 0.119 | 83
3C X 150 | 309 | 259 | 231 | 0.265 | 0.115 | 86
3C X 185 | 354 | 293 | 262 | 0.211 | 0.11 | 90
3C X 240 | 415 | 338 | 304 | 0.162 | 0.106 | 88
3C X 300 | 472 | 380 | 343 | 0.13 | 0.103 | 93
3C X 400 | 545 | 432 | 393 | 0.102 | 0.098 | 100

## Catalogue_CU (hidden)
LV Cable Catalogue (KEC/RPG Make Catalogue Attached) | [7 empty] | DERATING FACTORS
1-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | LV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) 4 trafoil groups, 6 tier trays with Touching |  | Ground temperature (35°C) (K3) | Depth of laying (900 mm) (K4) |  | Thermal resistivity of ground (1.2 K.m/W) (K5)
| Air | Ground | Duct | [6 empty] | Single core (Trefoil Formation with Touching) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 185 | 479 | 370 | 315 | 0.127 | 0.0875 | 27 | 690/400V | AIR | 1 | 0.9 | 0.66 | NA | NA | NA
1C X 240 | 569 | 424 | 350 | 0.0965 | 0.0866 | 29 |  | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98 | 1.5 | 1.09 | 1.05
1C X 300 | 659 | 470 | 389 | 0.0769 | 0.0857 | 32 |  | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98 | 2.5 | 1.09 | 1.05
1C X 400 | 769 | 556 | 466 | 0.0602 | 0.0855 | 36 |  | Trench with cover | 1 | 0.81 | 0.78 | NA | NA | NA | 4 | 1.09 | 1.05
1C X 500 | 877 | 620 | 518 | 0.0468 | 0.0851 | 40 | [8 empty] | 6 | 1.09 | 1.05
1C X 630 | 1013 | 695 | 555 | 0.0362 | 0.0843 | 44 | [8 empty] | 10 | 1.09 | 1.06
[15 empty] | 16 | 1.09 | 1.06
2-core cable |  |  |  |  | 0.6/1.0 kV (E) | [9 empty] | 25 | 1.09 | 1.08
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | [8 empty] | 35 | 1.09 | 1.08
| Air | Ground | Duct | [11 empty] | 50 | 1.09 | 1.08
2C X 1.5 | 29 | 33 | 29 | 15.5 | 0.108 | 12 | [8 empty] | 70 | 1.1 | 1.08
2C X 2.5 | 39 | 43 | 37 | 9.48 | 0.1007 | 13 | [8 empty] | 95 | 1.1 | 1.08
2C X 4 | 48 | 54 | 46 | 5.9 | 0.0947 | 14 | [8 empty] | 120 | 1.1 | 1.08
2C X 6 | 59 | 66 | 58 | 3.94 | 0.0902 | 15 | [8 empty] | 150 | 1.1 | 1.09
2C X 10 | 82 | 90 | 75 | 2.34 | 0.0852 | 17 | [8 empty] | 185 | 1.1 | 1.09
2C X 16 | 113 | 114 | 95 | 1.47 | 0.0815 | 18 | [8 empty] | 240 | 1.1 | 1.09
2C X 25 | 148 | 147 | 124 | 0.93 | 0.081 | 21 | [8 empty] | 300 | 1.1 | 1.09
2C X 35 | 186 | 177 | 152 | 0.671 | 0.0794 | 23 | [8 empty] | 400 | 1.11 | 1.1
2C X 50 | 221 | 210 | 185 | 0.495 | 0.0792 | 25 | [8 empty] | 500 | 1.11 | 1.1
2C X 70 | 278 | 260 | 228 | 0.319 | 0.0752 | 28 | [8 empty] | 630 | 1.11 | 1.1
2C X 95 | 338 | 309 | 277 | 0.247 | 0.0734 | 32
2C X 120 | 402 | 351 | 300 | 0.196 | 0.0726 | 34
2C X 150 | 461 | 392 | 341 | 0.159 | 0.0732 | 37
2C X 185 | 527 | 448 | 384 | 0.127 | 0.072 | 42
2C X 240 | 607 | 509 | 434 | 0.0965 | 0.0719 | 47
2C X 300 | 688 | 579 | 495 | 0.0769 | 0.0711 | 51
2C X 400 | 818 | 638 | 553 | 0.0602 | 0.0705 | 57
3-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
3C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
3C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 14
3C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 15
3C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 16
3C X 10 | 66 | 72 | 60 | 2.34 | 0.0852 | 19
3C X 16 | 85 | 95 | 79 | 1.47 | 0.0815 | 19
3C X 25 | 122 | 122 | 100 | 0.93 | 0.081 | 23
3C X 35 | 148 | 146 | 120 | 0.671 | 0.0794 | 24
3C X 50 | 181 | 175 | 151 | 0.495 | 0.0792 | 27
3C X 70 | 230 | 212 | 182 | 0.319 | 0.0752 | 32
3C X 95 | 284 | 253 | 211 | 0.247 | 0.0734 | 35
3C X 120 | 330 | 290 | 236 | 0.196 | 0.0726 | 37
3C X 150 | 375 | 325 | 271 | 0.159 | 0.0732 | 42
3C X 185 | 431 | 362 | 308 | 0.127 | 0.072 | 46
3C X 240 | 512 | 418 | 257 | 0.0965 | 0.0719 | 52
3C X 300 | 582 | 467 | 406 | 0.0769 | 0.0711 | 56
3C X 400 | 661 | 518 | 439 | 0.0602 | 0.0705 | 62
4-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
4C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
4C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
4C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
4C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
4C X 10 | 66 | 72 | 60 | 2.34 | 0.0852 | 20
4C X 16 | 85 | 95 | 79 | 1.47 | 0.0815 | 21
4C X 25 | 122 | 122 | 100 | 0.93 | 0.081 | 25
4C X 35 | 148 | 146 | 120 | 0.671 | 0.0794 | 27
4C X 50 | 181 | 175 | 151 | 0.495 | 0.0792 | 30
4C X 70 | 230 | 212 | 182 | 0.319 | 0.0752 | 36
4C X 95 | 284 | 253 | 211 | 0.247 | 0.0734 | 39
4C X 120 | 330 | 290 | 236 | 0.196 | 0.0726 | 43
4C X 150 | 375 | 325 | 271 | 0.159 | 0.0732 | 48
4C X 185 | 431 | 362 | 308 | 0.127 | 0.072 | 53
4C X 240 | 512 | 418 | 257 | 0.0965 | 0.0719 | 58
4C X 300 | 582 | 467 | 406 | 0.0769 | 0.0711 | 64
4C X 400 | 661 | 518 | 439 | 0.0602 | 0.0705 | 72
5-Core Cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
5C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108
5C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007
5C X 4 | 38 | 44 | 37 | 5.9 | 0.0947
5C X 6 | 51 | 55 | 46 | 3.94 | 0.0902
5C X 10 | 66 | 72 | 60 | 2.34 | 0.0852
5C X 16 | 85 | 95 | 79 | 1.47 | 0.0815
5C X 25 | 122 | 122 | 100 | 0.93 | 0.081
5C X 35 | 148 | 146 | 120 | 0.671 | 0.0794
5C X 50 | 181 | 175 | 151 | 0.495 | 0.0792
5C X 70 | 230 | 212 | 182 | 0.319 | 0.0752
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.121 | 26 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.116 | 27 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 417 | 323 | 308 | 0.196 | 0.111 | 29 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 473 | 361 | 343 | 0.159 | 0.109 | 30 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 543 | 406 | 387 | 0.128 | 0.105 | 33 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 641 | 469 | 447 | 0.098 | 0.101 | 35 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 735 | 526 | 504 | 0.079 | 0.1 | 38 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 845 | 590 | 564 | 0.063 | 0.096 | 41 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 942 | 640 | 608 | 0.05 | 0.095 | 47 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.093 | 51
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.09 | 55
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.088 | 59
Three core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.096 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.093 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.09 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.088 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.084 | 63
3C X 240 | 529 | 431 | 387 | 0.099 | 0.083 | 69
3C X 300 | 599 | 482 | 435 | 0.08 | 0.082 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.08 | 84
HV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 150mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1500 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.5 K.m/W) (K5) |  |  | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core | Single core | Single core | Multi core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.145 | 38 | 33000V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.139 | 40 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.95 | 120 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 120 | 417 | 323 | 308 | 0.196 | 0.133 | 41 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.96 | 150 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 150 | 473 | 361 | 343 | 0.159 | 0.132 | 44 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 185 | 543 | 406 | 387 | 0.128 | 0.126 | 46 | [8 empty] | 240 | 1.09 | 1.05 | 1.14 | 0.91 | 1.1 | 0.93
1C X 240 | 641 | 469 | 447 | 0.098 | 0.121 | 48 | [8 empty] | 300 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 300 | 735 | 526 | 504 | 0.079 | 0.118 | 50 | [8 empty] | 400 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 400 | 845 | 590 | 564 | 0.063 | 0.112 | 53 | [8 empty] | 500 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 500 | 942 | 640 | 608 | 0.05 | 0.108 | 57 | [8 empty] | 630 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.104 | 61
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.101 | 66
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.098 | 70
Three core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.129 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.123 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.118 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.115 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.11 | 63
3C X 240 | 529 | 431 | 387 | 0.99 | 0.105 | 69
3C X 300 | 599 | 482 | 435 | 0.8 | 0.103 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.098 | 84

## Catalogue Copper (hidden)
LV Cable Catalogue (KEC/RPG Make Catalogue Attached) | [7 empty] | DERATING FACTORS
1-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | LV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) 4 trafoil groups, 6 tier trays with Touching |  | Ground temperature (35°C) (K3) | Depth of laying (900 mm) (K4) |  | Thermal resistivity of ground (1.2 K.m/W) (K5)
| Air | Ground | Duct | [6 empty] | Single core (Trefoil Formation with Touching) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 185 | 479 | 370 | 315 | 0.127 | 0.0875 | 27 | 690/400V | AIR | 1 | 0.9 | 0.66 | NA | NA | NA
1C X 240 | 569 | 424 | 350 | 0.0965 | 0.0866 | 29 |  | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98 | 1.5 | 1.09 | 1.05
1C X 300 | 659 | 470 | 389 | 0.0769 | 0.0857 | 32 |  | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98 | 2.5 | 1.09 | 1.05
1C X 400 | 769 | 556 | 466 | 0.0602 | 0.0855 | 36 |  | Trench with cover | 1 | 0.81 | 0.78 | NA | NA | NA | 4 | 1.09 | 1.05
1C X 500 | 877 | 620 | 518 | 0.0468 | 0.0851 | 40 | [8 empty] | 6 | 1.09 | 1.05
1C X 630 | 1013 | 695 | 555 | 0.0362 | 0.0843 | 44 | [8 empty] | 10 | 1.09 | 1.06
[15 empty] | 16 | 1.09 | 1.06
2-core cable |  |  |  |  | 0.6/1.0 kV (E) | [9 empty] | 25 | 1.09 | 1.08
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | [8 empty] | 35 | 1.09 | 1.08
| Air | Ground | Duct | [11 empty] | 50 | 1.09 | 1.08
2C X 1.5 | 29 | 33 | 29 | 15.5 | 0.108 | 12 | [8 empty] | 70 | 1.1 | 1.08
2C X 2.5 | 39 | 43 | 37 | 9.48 | 0.1007 | 13 | [8 empty] | 95 | 1.1 | 1.08
2C X 4 | 48 | 54 | 46 | 5.9 | 0.0947 | 14 | [8 empty] | 120 | 1.1 | 1.08
2C X 6 | 59 | 66 | 58 | 3.94 | 0.0902 | 15 | [8 empty] | 150 | 1.1 | 1.09
2C X 10 | 82 | 90 | 75 | 2.34 | 0.0852 | 17 | [8 empty] | 185 | 1.1 | 1.09
2C X 16 | 113 | 114 | 95 | 1.47 | 0.0815 | 18 | [8 empty] | 240 | 1.1 | 1.09
2C X 25 | 148 | 147 | 124 | 0.93 | 0.081 | 21 | [8 empty] | 300 | 1.1 | 1.09
2C X 35 | 186 | 177 | 152 | 0.671 | 0.0794 | 23 | [8 empty] | 400 | 1.11 | 1.1
2C X 50 | 221 | 210 | 185 | 0.495 | 0.0792 | 25 | [8 empty] | 500 | 1.11 | 1.1
2C X 70 | 278 | 260 | 228 | 0.319 | 0.0752 | 28 | [8 empty] | 630 | 1.11 | 1.1
2C X 95 | 338 | 309 | 277 | 0.247 | 0.0734 | 32
2C X 120 | 402 | 351 | 300 | 0.196 | 0.0726 | 34
2C X 150 | 461 | 392 | 341 | 0.159 | 0.0732 | 37
2C X 185 | 527 | 448 | 384 | 0.127 | 0.072 | 42
2C X 240 | 607 | 509 | 434 | 0.0965 | 0.0719 | 47
2C X 300 | 688 | 579 | 495 | 0.0769 | 0.0711 | 51
2C X 400 | 818 | 638 | 553 | 0.0602 | 0.0705 | 57
3-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
3C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
3C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 14
3C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 15
3C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 16
3C X 10 | 66 | 72 | 60 | 2.34 | 0.0852 | 19
3C X 16 | 85 | 95 | 79 | 1.47 | 0.0815 | 19
3C X 25 | 122 | 122 | 100 | 0.93 | 0.081 | 23
3C X 35 | 148 | 146 | 120 | 0.671 | 0.0794 | 24
3C X 50 | 181 | 175 | 151 | 0.495 | 0.0792 | 27
3C X 70 | 230 | 212 | 182 | 0.319 | 0.0752 | 32
3C X 95 | 284 | 253 | 211 | 0.247 | 0.0734 | 35
3C X 120 | 330 | 290 | 236 | 0.196 | 0.0726 | 37
3C X 150 | 375 | 325 | 271 | 0.159 | 0.0732 | 42
3C X 185 | 431 | 362 | 308 | 0.127 | 0.072 | 46
3C X 240 | 512 | 418 | 257 | 0.0965 | 0.0719 | 52
3C X 300 | 582 | 467 | 406 | 0.0769 | 0.0711 | 56
3C X 400 | 661 | 518 | 439 | 0.0602 | 0.0705 | 62
4-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
4C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
4C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
4C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
4C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
4C X 10 | 66 | 72 | 60 | 2.34 | 0.0852 | 20
4C X 16 | 85 | 95 | 79 | 1.47 | 0.0815 | 21
4C X 25 | 122 | 122 | 100 | 0.93 | 0.081 | 25
4C X 35 | 148 | 146 | 120 | 0.671 | 0.0794 | 27
4C X 50 | 181 | 175 | 151 | 0.495 | 0.0792 | 30
4C X 70 | 230 | 212 | 182 | 0.319 | 0.0752 | 36
4C X 95 | 284 | 253 | 211 | 0.247 | 0.0734 | 39
4C X 120 | 330 | 290 | 236 | 0.196 | 0.0726 | 43
4C X 150 | 375 | 325 | 271 | 0.159 | 0.0732 | 48
4C X 185 | 431 | 362 | 308 | 0.127 | 0.072 | 53
4C X 240 | 512 | 418 | 257 | 0.0965 | 0.0719 | 58
4C X 300 | 582 | 467 | 406 | 0.0769 | 0.0711 | 64
4C X 400 | 661 | 518 | 439 | 0.0602 | 0.0705 | 72
5-Core Cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
5C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108
5C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007
5C X 4 | 38 | 44 | 37 | 5.9 | 0.0947
5C X 6 | 51 | 55 | 46 | 3.94 | 0.0902
5C X 10 | 66 | 72 | 60 | 2.34 | 0.0852
5C X 16 | 85 | 95 | 79 | 1.47 | 0.0815
5C X 25 | 122 | 122 | 100 | 0.93 | 0.081
5C X 35 | 148 | 146 | 120 | 0.671 | 0.0794
5C X 50 | 181 | 175 | 151 | 0.495 | 0.0792
5C X 70 | 230 | 212 | 182 | 0.319 | 0.0752
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.121 | 26 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.116 | 27 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 417 | 323 | 308 | 0.196 | 0.111 | 29 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 473 | 361 | 343 | 0.159 | 0.109 | 30 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 543 | 406 | 387 | 0.128 | 0.105 | 33 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 641 | 469 | 447 | 0.098 | 0.101 | 35 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 735 | 526 | 504 | 0.079 | 0.1 | 38 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 845 | 590 | 564 | 0.063 | 0.096 | 41 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 942 | 640 | 608 | 0.05 | 0.095 | 47 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.093 | 51
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.09 | 55
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.088 | 59
Three core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.096 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.093 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.09 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.088 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.084 | 63
3C X 240 | 529 | 431 | 387 | 0.099 | 0.083 | 69
3C X 300 | 599 | 482 | 435 | 0.08 | 0.082 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.08 | 84
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.121 | 26 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.116 | 27 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 417 | 323 | 308 | 0.196 | 0.111 | 29 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 473 | 361 | 343 | 0.159 | 0.109 | 30 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 543 | 406 | 387 | 0.128 | 0.105 | 33 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 641 | 469 | 447 | 0.098 | 0.101 | 35 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 735 | 526 | 504 | 0.079 | 0.1 | 38 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 845 | 590 | 564 | 0.063 | 0.096 | 41 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 942 | 640 | 608 | 0.05 | 0.095 | 47 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.093 | 51
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.09 | 55
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.088 | 59
Three core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.096 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.093 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.09 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.088 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.084 | 63
3C X 240 | 529 | 431 | 387 | 0.099 | 0.083 | 69
3C X 300 | 599 | 482 | 435 | 0.08 | 0.082 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.08 | 84
HV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 150mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1500 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.5 K.m/W) (K5) |  |  | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core | Single core | Single core | Multi core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.145 | 38 | 33000V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.139 | 40 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.95 | 120 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 120 | 417 | 323 | 308 | 0.196 | 0.133 | 41 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.96 | 150 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 150 | 473 | 361 | 343 | 0.159 | 0.132 | 44 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 185 | 543 | 406 | 387 | 0.128 | 0.126 | 46 | [8 empty] | 240 | 1.09 | 1.05 | 1.14 | 0.91 | 1.1 | 0.93
1C X 240 | 641 | 469 | 447 | 0.098 | 0.121 | 48 | [8 empty] | 300 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 300 | 735 | 526 | 504 | 0.079 | 0.118 | 50 | [8 empty] | 400 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 400 | 845 | 590 | 564 | 0.063 | 0.112 | 53 | [8 empty] | 500 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 500 | 942 | 640 | 608 | 0.05 | 0.108 | 57 | [8 empty] | 630 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.104 | 61
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.101 | 66
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.098 | 70
Three core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.129 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.123 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.118 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.115 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.11 | 63
3C X 240 | 529 | 431 | 387 | 0.99 | 0.105 | 69
3C X 300 | 599 | 482 | 435 | 0.8 | 0.103 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.098 | 84

## Tray-Void (hidden)
APCh-CPP-CABLE TRAY BOQ
[6 empty] | Inside Electrical room-Cable celler (GF) | [6 empty] | Inside Electrical room-Cable celler (SF) |  |  |  | For outside rack upto electrical room - north side | [9 empty] | For outside rack upto electrical room - north side to south side rack upto HRSG | [5 empty] | from Rack to BSDG Building
Voltage | Tray Type | Tray size | NOS | no. of motors | Purpose | Inside electrical room cable cellar (below GTG Panel) | Inside electrical room cable cellar (below STG Panel) | Inside electrical room cable cellar (below 6.6kv Panel) | Inside electrical room cable cellar CROSSING (below 6.6kv Panel) | Inside electrical room cable cellar (below 33kv Panel) | Inside electrical room cable cellar Crossing (below 33kv Panel) | Battery room side | Inside electrical room 2nd floor cable cellar (below 150kv Panel) | Inside electrical room dropper (below 150kv Panel) | Inside electrical room 2nd floor cable cellar (150kv Control) | raiser & droppers | from electrical building edge to north side pipe rack connecting | Rack on front side Electrical building | from electrical building edge to north side pipe rack connecting | from north side pipe rack to north & south side pipe rack connectivity | from north & south side pipe rack to GTG -1 Electrical room crossing | from north side pipe to crossing towards GTG -1 side to Electrical room (GTG-1) | from pipe rack crossing GTG -1 side to GTG-2 crossing pipe rack | from crossing pipe rack towards GTG -2 side to Electrical room (GTG-2) | crossing from celler to STG | Crossing from rack to STG package | from north side pipe rack to south side side pipe rack connectivity towards HRSG-1 side | from north side pipe rack to STG Pckage | from south side side pipe rack connectivity towards HRSG-1 | from south side side pipe rack crossing to HRSG-1 area | From South side HRSG - to HRSG-2 crossing | from south side side pipe rack crossing HRSG-2 to HRSG area | from north side pipe rack to BSDG Building | from Rack to inside building | dropping near equipment | Total Quantity
Route no. | [5 empty] | EB-1 | EB-2 | EB-3 | EB-3A | EB-4 | EB-4A | EB-4B+C | EB-5 | EB-5A | EB-5B |  | OSN-1 | OSN-2 | OSN-3 | OSN-4 | OSN-5 | OSN-6 | OSN-7 | OSN-8 | OSN-8A | OSN-8B | OSS-1 | OSS-1A | OSS-2 | OSS-3 | OSS-4 | OSS-5 | OSB-1 | OSB-2
Length | [5 empty] | 43 | 43 | 34 | 11 | 34 | 6 | 20 | 23 | 10 | 34 | 20 | 12 | 15 | 12 | 32 | 45 | 26 | 40 | 26 | 15 | 25 | 105 | 35 | 26 | 36 | 40 | 36 | 115 | 15 | 3
Purpose | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cable Trays for Electrical Power Cable
150kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
150kV-P | Ladder | L-600 | 1 |  | GSUT | [7 empty] | 23 | 10 |  | 20 |  |  | 12 | 32 | 45 |  | 40 | [11 empty] | 0 | 182
150kV-P | Ladder | L-300 | 1 | [12 empty] | 20 | [5 empty] | 26 |  | 26 | [10 empty] | 0 | 72
150kV-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
150kV-P | Ladder | L-150 | 1 | 2 | GSUT | [29 empty] | 6 | 6
150kV-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
[35 empty] | 0 | 0
[35 empty] | 0 | 0
33kV-P | Ladder | L-600 | 2 | [6 empty] | 68 | 12 | [23 empty] | 0 | 80
33kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
[35 empty] | 0 | 0
6.6kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
6.6kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
6.6kV-P | Ladder | L-600 | 1 |  | 6.6kv Incoming-BSDG |  |  | 34 | 11 | [6 empty] | 20 | 12 | 15 | 12 | 32 | [12 empty] | 105 | 26 | 0 | 267
6.6kV-P | Ladder | L-600 | 1 |  | 6.6kv motors |  |  | 34 | 11 | [6 empty] | 20 | 12 | 15 | 12 | 32 | [14 empty] | 0 | 136
6.6kV-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
6.6kV-P | Ladder | L-300 | 1 | [12 empty] | 20 | [5 empty] | 26 |  | 26 | [10 empty] | 0 | 72
6.6kV-P | Ladder | L-150 | 1 | 6 | [30 empty] | 18 | 18
6.6kV-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
[35 empty] | 0 | 0
LV GTG-P | Ladder | L-600 | 2 |  | GTG Panels | 86 | [9 empty] | 40 |  | 24 | 64 | 90 | 52 | [13 empty] | 0 | 356
LV GTG-P | Ladder | L-600 | 1 | [12 empty] | 20 | [5 empty] | 40 | 26 | 26 | [10 empty] | 0 | 112
LV GTG-P | Ladder | L-300 | 1 | 4 | [30 empty] | 12 | 12
LV GTG-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
LV GTG-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
LV GTG-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
[35 empty] | 0 | 0
LV STG-P | Ladder | L-600 | 3 |  | STG Motors |  | 129 | [27 empty] | 0 | 129
LV STG-P | Ladder | L-600 | 2 | [12 empty] | 40 | 24 | 30 | 24 | 64 | [7 empty] | 70 | [6 empty] | 0 | 252
LV STG-P | Ladder | L-600 | 1 | [12 empty] | 20 | [8 empty] | 15 | 25 | [8 empty] | 0 | 60
LV STG-P | Ladder | L-300 | 1 | [12 empty] | 20 | [8 empty] | 15 | 25 | [8 empty] | 0 | 60
LV STG-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
LV STG-P | Ladder | L-150 | 1 | 23 | Droppets | [29 empty] | 69 | 69
LV STG-P | Ladder | L-150 | 1 | 41 | [30 empty] | 123 | 123
[35 empty] | 0 | 0
Cable Trays for Electrical control Cable
LV -C | Perforated | P-600 | 1 |  |  | 43 | 43 | 34 | 11 | 34 | 6 |  | 23 | 10 | 34 | 20 | 12 | 15 | 12 | 32 | 45 |  | 40 | 26 |  |  |  | 35 | [6 empty] | 0 | 475
LV -C | Perforated | P-300 | 1 | [5 empty] | 11 |  | 6 | 20 |  |  |  | 20 | [5 empty] | 26 |  | 26 | 15 | 25 | 105 |  | 26 | 36 | 40 | 36 | 115 | 15 | 0 | 522
LV -C | Perforated | P-300 | 1 | [31 empty] | 0 | 0
LV -C | Perforated | P-150 | 1 | [8 empty] | 20 | [9 empty] | 26 |  | 26 | [10 empty] | 0 | 72
LV -C | Perforated | P-150 | 1 | [31 empty] | 0 | 0
3075
Tray Type |  | Size | Quantity in Mtrs | Quantity with 5% margin in Mtrs | Horizontal Bends (Nos) | Vertical Bends (Nos) | Tee Bends (Nos) | Reducer (Nos) |  | Tray Support C-CHANNEL: (75*40*40*6)mm Mtrs | Tray Support ANGLE: (50*50*6)mm mtrs
Ladder Type Cable Tray |  | L-600 | 1574 | 1653 | 78.7 | 47.22 | 47.22 | 47.22 |  | 794 | 218
Ladder Type Cable Tray |  | L-300 | 216 | 227 | 10.8 | 6.48 | 6.48 | 6.48
Ladder Type Cable Tray |  | L-150 | 216 | 227 | 10.8 | 6.48 | 6.48
Perforated Type Cable Tray |  | P-600 | 475 | 499 | 23.75 | 14.25 | 14.25 | 14.25
Perforated Type Cable Tray |  | P-300 | 522 | 549 | 26.1 | 15.66 | 15.66 | 15.66
Perforated Type Cable Tray |  | P-150 | 72 | 76 | 3.6 | 2.16 | 2.16
Perforated Type Cable Tray -Cover |  | P-600 | 475 | 499 |  |  |  | 14.25
Perforated Type Cable Tray -Cover |  | P-300 | 459 | 482 |  |  |  | 13.77

## requred Dia (hidden)
BSDG
| inside | outside | outside | outside | outside
GTG requred | 1200mm | 1200 | 600 | 600
STG requred | 1800mm | 1800 | 900 | 900
6.6kv | 1200 | 600 | 300 | 300 | 600
33kV | 1200
150kV | 600 | 600 | 300 | 300

## Sheet1 (hidden)
Cable Tray Sections | Tray Size | UOM | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | G1 | G2 | G3 | G4 | H | I | J | J1 | J2 | J3 | K | L | L1 | L2 | L3 | L4 | M | N | O | O1 | P | Q | Q1 | Q2 | Q3 | R | R1 | R2 | S | T
Instrumentation Cable Trays
IS Cable Tray | Total Cable Dia
| 600 | Nos
| 450 | Nos
| 300 | Nos
Non IS Cable Tray | Total Cable Dia
| 600 | Nos
| 450 | Nos
| 300 | Nos
F&G Cable Tray | Total Cable Dia
| 600 | Nos
| 450 | Nos
| 300 | Nos
FOC & Telecom Cable Tray | Total Cable Dia
| 600 | Nos
| 450 | Nos
| 300 | Nos

## Tray-S_old (hidden)
sl No. | Section | Toute | Equipments | feeder no. | no. of runs each feeder | size | dia of each cable | Total no. of runs | total dia require | Tray Size | Total Treay requirement | no of Trays
1 | K-K | towards Electrolyser | 33kV Electrolyzer rectifier Trafo | 32 | 1 | 3C x 150 Sqmm | 86 | 32 | 2752 | 600 | 4.5867 | 5
1 | A-A | towards CT & OTHER SS | 11KV T/F & Motor | 25 | 1 | 3C x 95 Sqmm | 55 | 25 | 1375 | 600 | 2.2917 | 3
1 | B-B | towards NH3 & OTHER SS | 11KV T/F & Motor | 17 | 1 | 3C x 95 Sqmm | 55 | 17 | 935 | 600 | 1.5583 | 2
[5 empty] | 3 | 2
|  |  |  | 14 |  |  | 8+(8+3)
3750
|  | 2300 |  |  | 3 | 13
1450
[7 empty] | B | C
[7 empty] | 19 | 15
5.6